## Inputs
Line-Energy Solar Calculator | v0.3.0-draft
Input | Value | Unit | Notes
Inverter model | SUN-8K-SG01LP1-EU |  | Must match Inverters!C:C
Panel model | JKM575N-72HL4-V |  | Must match Panels!C:C
Minimum ambient temperature | -10 | C | Used for cold Voc check
Maximum cell temperature | 70 | C | Used for hot Vmp check
Panels per string | 8 | pcs | Series modules in one string
Strings per MPPT | 1 | pcs | Parallel strings on one tracker
Design note | Starter calculation only |  | Verify datasheets before commercial use

## Results
Result | Value | Unit | Formula / meaning
Inverter model |  |  | From Inputs
Panel model |  |  | From Inputs
Panels per string |  | pcs | From Inputs
Strings per MPPT |  | pcs | From Inputs
Max PV voltage |  | V | Inverter absolute PV voltage limit
MPPT min voltage |  | V | Inverter lower MPPT voltage
MPPT max voltage |  | V | Inverter upper MPPT voltage
Max input current per MPPT |  | A | Inverter current limit
Panel Voc STC |  | V | Open-circuit voltage at STC
Panel Vmp STC |  | V | Voltage at maximum power at STC
Panel Imp STC |  | A | Current at maximum power at STC
Panel Voc temperature coefficient |  | %/C | Used for preliminary voltage correction
Cold string Voc |  | V | Voc at minimum temperature
Hot string Vmp |  | V | Preliminary Vmp at maximum cell temperature
MPPT operating check |  |  | Hot Vmp must stay inside MPPT window
Max voltage check |  |  | Cold Voc must stay below max PV voltage
Current check |  |  | Parallel string current must stay below MPPT current
Overall preliminary status |  |  | All checks must pass

## Inverters
brand | series | model | phase | nominal_ac_power_w | max_pv_input_power_w | max_pv_voltage_v | startup_voltage_v | mppt_voltage_min_v | mppt_voltage_max_v | mppt_count | strings_per_mppt | max_input_current_per_mppt_a | max_short_circuit_current_per_mppt_a | battery_nominal_voltage_v | battery_voltage_range_v | data_status | notes
Deye | LV Hybrid | SUN-3.6K-SG03LP1-EU | single-phase | 3600 | 4680 | 500 | 150 | 125 | 425 | 2 | 1+1 | 13 | 17 | 48 | 40-60 | seed_verify_datasheet | Starter record for low-voltage hybrid inverter calculations.
Deye | LV Hybrid | SUN-5K-SG03LP1-EU | single-phase | 5000 | 6500 | 500 | 150 | 125 | 425 | 2 | 1+1 | 13 | 17 | 48 | 40-60 | seed_verify_datasheet | Starter record for low-voltage hybrid inverter calculations.
Deye | LV Hybrid | SUN-6K-SG03LP1-EU | single-phase | 6000 | 7800 | 500 | 150 | 125 | 425 | 2 | 1+1 | 13 | 17 | 48 | 40-60 | seed_verify_datasheet | Starter record for low-voltage hybrid inverter calculations.
Deye | LV Hybrid | SUN-8K-SG01LP1-EU | single-phase | 8000 | 10400 | 500 | 150 | 125 | 425 | 2 | 2+2 | 26 | 34 | 48 | 40-60 | seed_verify_datasheet | Starter record; verify exact PV current and string inputs for selected market version.

## Panels
brand | series | model | power_stc_w | vmp_stc_v | imp_stc_a | voc_stc_v | isc_stc_a | temp_coeff_pmax_pct_c | temp_coeff_voc_pct_c | temp_coeff_isc_pct_c | module_length_mm | module_width_mm | module_depth_mm | data_status | notes
Jinko | Tiger Neo N-type 72HL4 | JKM565N-72HL4-V | 565 | 43.28 | 13.06 | 51.7 | 13.86 | -0.29 | -0.25 | 0.045 | 2278 | 1134 | 30 | seed_verify_datasheet | Starter record for string sizing tests.
Jinko | Tiger Neo N-type 72HL4 | JKM570N-72HL4-V | 570 | 43.52 | 13.1 | 51.89 | 13.89 | -0.29 | -0.25 | 0.045 | 2278 | 1134 | 30 | seed_verify_datasheet | Starter record for string sizing tests.
Jinko | Tiger Neo N-type 72HL4 | JKM575N-72HL4-V | 575 | 43.76 | 13.14 | 52.08 | 13.92 | -0.29 | -0.25 | 0.045 | 2278 | 1134 | 30 | seed_verify_datasheet | Starter record for string sizing tests.
Jinko | Tiger Neo N-type 72HL4 | JKM580N-72HL4-V | 580 | 43.99 | 13.19 | 52.27 | 13.96 | -0.29 | -0.25 | 0.045 | 2278 | 1134 | 30 | seed_verify_datasheet | Starter record for string sizing tests.
Jinko | Tiger Neo N-type 72HL4 | JKM585N-72HL4-V | 585 | 44.23 | 13.23 | 52.46 | 14 | -0.29 | -0.25 | 0.045 | 2278 | 1134 | 30 | seed_verify_datasheet | Starter record for string sizing tests.
LONGi | Hi-MO 6 | LR5-72HTH-565M | 565 | 42.94 | 13.16 | 51.21 | 14.01 | -0.29 | -0.23 | 0.05 | 2278 | 1134 | 35 | seed_verify_datasheet | Starter record for string sizing tests.
LONGi | Hi-MO 6 | LR5-72HTH-570M | 570 | 43.13 | 13.22 | 51.4 | 14.07 | -0.29 | -0.23 | 0.05 | 2278 | 1134 | 35 | seed_verify_datasheet | Starter record for string sizing tests.
LONGi | Hi-MO 6 | LR5-72HTH-575M | 575 | 43.32 | 13.28 | 51.59 | 14.14 | -0.29 | -0.23 | 0.05 | 2278 | 1134 | 35 | seed_verify_datasheet | Starter record for string sizing tests.
LONGi | Hi-MO 6 | LR5-72HTH-580M | 580 | 43.51 | 13.34 | 51.78 | 14.2 | -0.29 | -0.23 | 0.05 | 2278 | 1134 | 35 | seed_verify_datasheet | Starter record for string sizing tests.
LONGi | Hi-MO 6 | LR5-72HTH-585M | 585 | 43.7 | 13.39 | 51.97 | 14.26 | -0.29 | -0.23 | 0.05 | 2278 | 1134 | 35 | seed_verify_datasheet | Starter record for string sizing tests.