## Summary
Конструктор Line-Energy Solar (Line-Energy Solar Designer) | v0.22.0-draft
Показатель (Item) | Значение (Value) | Ед. изм. (Unit) | Статус / примечание (Status / Note)
Общая совместимость (Overall compatibility) |  |  | PASS / FAIL / VERIFY
Электрический статус PV (PV electrical status) |  |  | Из листа Results (From Results)
Статус АКБ (Battery status) |  |  | Из листа Compatibility (From Compatibility)
Полнота datasheet (Datasheet completeness) |  |  | Из листа Compatibility (From Compatibility)
Инвертор (Inverter) |  |  | Выбранная модель (Selected model)
Панель (Panel) |  |  | Выбранная модель (Selected model)
АКБ (Battery) |  |  | Выбранная модель (Selected model)
Панелей в строке (Panels per string) |  | pcs | Выбранное значение (Selected value)
Рекомендуемый диапазон строки (Recommended string range) |  | pcs | Calculated range
Общая энергия АКБ (Battery total energy) |  | kWh | Номинальная энергия (Nominal energy)
Тип кровли (Roof type) |  |  | Выбранная кровля (Selected roof)
Всего панелей (Total panels) |  | pcs | Ввод для крепежа (Mounting input)
Ряды (Rows) |  | rows | Расчет крепежа (Mounting calculation)
Рейки (Rails) |  | pcs | Расчет крепежа (Mounting calculation)
Крайние прижимы (End clamps) |  | pcs | Расчет крепежа (Mounting calculation)
Средние прижимы (Middle clamps) |  | pcs | Расчет крепежа (Mounting calculation)
Клипсы заземления (Grounding clips) |  | pcs | Расчет крепежа (Mounting calculation)
Кабельные клипсы (Cable clips) |  | pcs | Расчет крепежа (Mounting calculation)
Позиций оборудования (Equipment list items) |  | items | Сформированный список оборудования (Generated equipment output)
Позиций защиты (Protection items) |  | items | Сформированный список защиты (Generated protection output)
Сечение DC кабеля (DC cable section) |  | mm2 | Стартовый подбор (Starter sizing)
Сечение AC кабеля (AC cable section) |  | mm2 | Стартовый подбор (Starter sizing)
Сечение кабеля АКБ (Battery cable section) |  | mm2 | Стартовый подбор (Starter sizing)
Рекомендация УЗИП (SPD recommendation) |  |  | Стартовый выбор защиты (Starter protection selection)
Система заземления (Earthing system) |  |  | Выбранная система заземления AC (Selected AC earthing system)
Коэффициент снижения нагрузки кабеля (Cable derating factor) |  | factor | Группировка x температурные коэффициенты (Grouping x ambient factors)
Массовые сценарии (Bulk scenarios) |  | rows | Mass compatibility table
Массовые PASS (Bulk PASS) |  | rows | Bulk compatibility count
Массовые FAIL (Bulk FAIL) |  | rows | Bulk compatibility count
Массовые VERIFY (Bulk VERIFY) |  | rows | Bulk compatibility count
Регион (Region) |  |  | Economics input
Годовая выработка (Annual generation) |  | kWh/year | Оценка региональной выработки (Regional yield estimate)
Годовая экономия (Annual savings) |  | RUB/year | Собственное потребление плюс экспорт (Self-consumption plus export)
Простая окупаемость (Simple payback) |  | years | Стоимость системы / годовая экономия (Installed cost / annual savings)
Статус источника тарифа (Tariff source status) |  |  | Нужно проверить (Must be verified)
Потребление в месяц (Monthly consumption) |  | kWh/month | Ввод клиента (Customer input)
Целевое покрытие (Target coverage) |  | % | Цель подбора варианта (Option sizing target)
Рекомендуемая стандартная мощность (Recommended standard size) |  | kWp | Лист SystemOptions (SystemOptions)
Годовая выработка стандартного варианта (Standard option annual generation) |  | kWh/year | Лист SystemOptions (SystemOptions)
Окупаемость стандартного варианта день-ночь (Standard option payback day-night) |  | years | Лист SystemOptions (SystemOptions)
Выработка в лучший месяц (Best month generation) |  | kWh/month | MonthlyGeneration
Выработка в худший месяц (Worst month generation) |  | kWh/month | MonthlyGeneration
Ценность собственного потребления по месяцам (Monthly self-consumption value) |  | RUB/year | MonthlyGeneration
Ценность экспорта по месяцам (Monthly export value) |  | RUB/year | MonthlyGeneration

## Inputs
Калькулятор Line-Energy Solar (Line-Energy Solar Calculator) | v0.22.0-draft
Ввод (Input) | Значение (Value) | Ед. изм. (Unit) | Примечания (Notes)
Модель инвертора (Inverter model) | SUN-8K-SG01LP1-EU |  | Выберите из списка (Choose from dropdown)
Модель панели (Panel model) | JKM575N-72HL4-V |  | Выберите из списка (Choose from dropdown)
Минимальная температура воздуха (Minimum ambient temperature) | -10 | C | Для проверки Voc на холоде (Used for cold Voc check)
Максимальная температура ячейки (Maximum cell temperature) | 70 | C | Для проверки Vmp на нагреве (Used for hot Vmp check)
Панелей в строке (Panels per string) | 8 | pcs | Модули последовательно в одной строке (Series modules in one string)
Строк на MPPT (Strings per MPPT) | 1 | pcs | Параллельные строки на один трекер (Parallel strings on one tracker)
Модель АКБ (Battery model) | US5000 |  | Выберите из списка (Choose from dropdown)
Количество АКБ (Battery quantity) | 2 | pcs | Для расчета общей емкости АКБ (Used for total battery capacity)
Тип кровли (Roof type) | Metal tile |  | Выберите из списка (Choose from dropdown)
Всего панелей (Total panels) | 16 | pcs | Для расчета количества крепежа (Used for mounting quantity calculation)
Панелей в ряду (Panels per row) | 8 | pcs | Для расчета рядов и прижимов (Used for row and clamp calculation)
Длина рейки со склада (Rail stock length) | 4.2 | m | Для оценки соединителей рейки (Used for rail connector estimate)
Длина рейки на панель (Rail length per panel) | 1.15 | m | Стартовое допущение; уточнить по ориентации панели (Starter assumption; adjust by panel orientation)
Запас крепежа (Mounting reserve) | 10 | % | Дополнительный запас количества (Extra quantity reserve)
Длина DC кабеля (DC cable route length) | 30 | m | Оценка длины трассы в одну сторону (One-way route length estimate)
Длина AC кабеля (AC cable route length) | 20 | m | Оценка длины трассы в одну сторону (One-way route length estimate)
Длина кабеля заземления (Grounding cable route length) | 25 | m | Grounding route length estimate
Способ прокладки (Installation method) | Open air |  | Для примечаний по снижению нагрузки кабеля (Used for cable derating notes)
Коэффициент группировки кабелей (Cable grouping derating) | 1 | factor | Стартовый коэффициент; уточнить по местным нормам (Starter factor; adjust by local rules)
Коэффициент температуры окружающей среды (Ambient temperature derating) | 1 | factor | Стартовый коэффициент; уточнить по местным нормам (Starter factor; adjust by local rules)
Система молниезащиты (Lightning protection system) | No external LPS |  | Для рекомендации типа УЗИП (Used for SPD type suggestion)
Система заземления AC (AC earthing system) | TN-S |  | Для чек-листа заземления (Used for earthing checklist)
Регион / тарифная зона (Region / tariff zone) | Moscow starter |  | Выберите из базы тарифов (Choose from tariff database)
Доля собственного потребления (Self-consumption share) | 70 | % | Доля выработки, потребляемая на объекте (Share of generation consumed on site)
Стоимость установленной системы (Installed system cost) | 800000 | RUB | Для оценки простой окупаемости (Used for simple payback estimate)
Статус источника тарифа (Tariff source status) | VERIFY |  | Тарифы нужно сверить по поставщику и дате (Tariffs must be checked for exact supplier/date)
Потребление в месяц (Monthly consumption) | 1000 | kWh/month | Месячное потребление клиента (Customer monthly electricity consumption)
Целевое покрытие (Target coverage) | 70 | % | Рекомендуемые варианты покрывают эту долю годового потребления (Recommended options cover this share of annual consumption)
Режим тарифа (Tariff mode) | Single-rate |  | Сравнение единого тарифа и день-ночь (Single-rate or Day-night comparison)
Доля дневного потребления (Day consumption share) | 65 | % | Для сравнения тарифа день-ночь (Used for day-night tariff comparison)
Дневной тариф (Day tariff) | 9.8 | RUB/kWh | Стартовый дневной тариф; сверить поставщика/дату (Starter day tariff; verify supplier/date)
Ночной тариф (Night tariff) | 3.5 | RUB/kWh | Стартовый ночной тариф; сверить поставщика/дату (Starter night tariff; verify supplier/date)
Примечание по расчету (Design note) | Только стартовый расчет (Starter calculation only) |  | Проверить datasheet и инструкции по крепежу перед коммерческим применением (Verify datasheets and mounting manuals before commercial use)

## Results
Результат (Result) | Значение (Value) | Ед. изм. (Unit) | Формула / смысл (Formula / meaning)
Модель инвертора (Inverter model) |  |  | Из листа Inputs (From Inputs)
Модель панели (Panel model) |  |  | Из листа Inputs (From Inputs)
Панелей в строке (Panels per string) |  | pcs | Из листа Inputs (From Inputs)
Строк на MPPT (Strings per MPPT) |  | pcs | Из листа Inputs (From Inputs)
Max PV voltage |  | V | Inverter absolute PV voltage limit
MPPT min voltage |  | V | Inverter lower MPPT voltage
MPPT max voltage |  | V | Inverter upper MPPT voltage
Max input current per MPPT |  | A | Inverter current limit
Panel Voc STC |  | V | Open-circuit voltage at STC
Panel Vmp STC |  | V | Voltage at maximum power at STC
Panel Imp STC |  | A | Current at maximum power at STC
Panel voltage temperature coefficient |  | %/C | Preliminary voltage correction
Cold Voc per panel |  | V | Voc at minimum temperature
Hot Vmp per panel |  | V | Vmp at maximum cell temperature
Cold string Voc |  | V | Cold Voc per panel x panels per string
Hot string Vmp |  | V | Hot Vmp per panel x panels per string
Minimum panels per string by MPPT |  | pcs | Ceiling of MPPT min / hot Vmp per panel
Maximum panels per string by MPPT |  | pcs | Floor of MPPT max / hot Vmp per panel
Maximum panels per string by PV voltage |  | pcs | Floor of max PV voltage / cold Voc per panel
Recommended panels per string range |  | pcs | Minimum to safest maximum
MPPT operating check |  |  | Hot Vmp must stay inside MPPT window
Max voltage check |  |  | Cold Voc must stay below max PV voltage
Current check |  |  | Parallel string current must stay below MPPT current
Overall preliminary status |  |  | All checks must pass
Модель АКБ (Battery model) |  |  | Из листа Inputs (From Inputs)
Количество АКБ (Battery quantity) |  | pcs | Из листа Inputs (From Inputs)
Battery nominal energy |  | kWh | Из базы Batteries (From Batteries database)
Total nominal battery energy |  | kWh | Battery energy x quantity
Battery compatibility note |  |  | Из базы Batteries (From Batteries database)

## Inverters
brand | series | model | phase | nominal_ac_power_w | max_pv_input_power_w | max_pv_voltage_v | startup_voltage_v | mppt_voltage_min_v | mppt_voltage_max_v | mppt_count | strings_per_mppt | max_input_current_per_mppt_a | max_short_circuit_current_per_mppt_a | battery_nominal_voltage_v | battery_voltage_range_v | data_status | notes
Anenji | Hybrid | ANJ-3.2KW-24V | single-phase | 3200 | [9 empty] | 24 |  | model_only_needs_datasheet | Hybrid inverter model candidate; datasheet parameters pending.
Anenji | Hybrid | ANJ-3.6KW-24V | single-phase | 3600 | [9 empty] | 24 |  | model_only_needs_datasheet | Hybrid inverter model candidate; datasheet parameters pending.
Anenji | Hybrid | ANJ-4.2KW-24V | single-phase | 4200 | [9 empty] | 24 |  | model_only_needs_datasheet | Hybrid inverter model candidate; datasheet parameters pending.
Anenji | Hybrid | ANJ-6.2KW-48V | single-phase | 6200 | [9 empty] | 48 |  | model_only_needs_datasheet | Hybrid inverter model candidate; datasheet parameters pending.
Anenji | Hybrid | ANJ-8.2KW-48V | single-phase | 8200 | [9 empty] | 48 |  | model_only_needs_datasheet | Hybrid inverter model candidate; datasheet parameters pending.
Anenji | Hybrid | ANJ-10.2KW-48V | single-phase | 10200 | [9 empty] | 48 |  | model_only_needs_datasheet | Hybrid inverter model candidate; datasheet parameters pending.
Anenji | Hybrid | ANJ-11KW-48V | single-phase | 11000 | [9 empty] | 48 |  | model_only_needs_datasheet | Hybrid inverter model candidate; datasheet parameters pending.
Anenji | Hybrid | ANJ-12KW-48V | single-phase | 12000 | [9 empty] | 48 |  | model_only_needs_datasheet | Hybrid inverter model candidate; datasheet parameters pending.
Deye | Hybrid LV 24V | SUN-3K-SG04LP1-24-EU | single-phase | 3000 | [9 empty] | 24 |  | model_only_needs_datasheet | Model list provided by user; datasheet parameters pending.
Deye | Hybrid LV | SUN-3K-SG04LP1-EU | single-phase | 3000 | [9 empty] | 48 |  | model_only_needs_datasheet | Model list provided by user; datasheet parameters pending.
Deye | Hybrid LV | SUN-3.6K-SG05LP1-EU-AM2-P | single-phase | 3600 | 7200 | 500 | 125 | 150 | 425 | 2 | 2+2 | 32 | 48 | 48 | 40-60 | datasheet_local_pdf_verified | Local PDF: SUN-_3.6-10_K-SG05LP1-EU-AM2-P_RU.pdf
Deye | Hybrid LV | SUN-5K-SG05LP1-EU-AM2-P | single-phase | 5000 | 10000 | 500 | 125 | 150 | 425 | 2 | 2+2 | 32 | 48 | 48 | 40-60 | datasheet_local_pdf_verified | Local PDF: SUN-_3.6-10_K-SG05LP1-EU-AM2-P_RU.pdf
Deye | Hybrid LV | SUN-6K-SG05LP1-EU-AM2-P | single-phase | 6000 | 12000 | 500 | 125 | 150 | 425 | 2 | 2+2 | 32 | 48 | 48 | 40-60 | datasheet_local_pdf_verified | Local PDF: SUN-_3.6-10_K-SG05LP1-EU-AM2-P_RU.pdf
Deye | Hybrid LV | SUN-8K-SG05LP1-EU-AM2-P | single-phase | 8000 | 16000 | 500 | 125 | 150 | 425 | 2 | 2+2 | 32 | 48 | 48 | 40-60 | datasheet_local_pdf_verified | Local PDF: SUN-_3.6-10_K-SG05LP1-EU-AM2-P_RU.pdf
Deye | Hybrid LV | SUN-10K-SG02LP1-EU-AM3-P | single-phase | 10000 | 20000 | 500 | 125 | 150 | 425 | 3 | 2+2+2 | 32 | 60 | 48 | 40-60 | datasheet_local_pdf_verified | Local PDF: SUN-_7.6-12_K-SG02LP1-EU-AM2-P_RU.pdf
Deye | Hybrid LV | SUN-12K-SG02LP1-EU-AM3-P | single-phase | 12000 | 24000 | 500 | 125 | 150 | 425 | 3 | 2+2+2 | 32 | 60 | 48 | 40-60 | datasheet_local_pdf_verified | Local PDF: SUN-_7.6-12_K-SG02LP1-EU-AM2-P_RU.pdf
Deye | Hybrid LV | SUN-14K-SG01LP1-EU-AM3-P | single-phase | 14000 | 28000 | 500 | 125 | 150 | 425 | 3 | 2+2+2 | 36 | 54 | 48 | 40-60 | datasheet_local_pdf_verified | Local PDF: SUN-_12-18_K-SG01LP1-EU-AM3-P_RU.pdf
Deye | Hybrid LV | SUN-16K-SG01LP1-EU-AM3-P | single-phase | 16000 | 32000 | 500 | 125 | 150 | 425 | 3 | 2+2+2 | 36 | 54 | 48 | 40-60 | datasheet_local_pdf_verified | Local PDF: SUN-_12-18_K-SG01LP1-EU-AM3-P_RU.pdf
Deye | Hybrid LV | SUN-18K-SG01LP1-EU-AM3-P | single-phase | 18000 | 36000 | 500 | 125 | 150 | 425 | 3 | 2+2+2 | 36 | 54 | 48 | 40-60 | datasheet_local_pdf_verified | Local PDF: SUN-_12-18_K-SG01LP1-EU-AM3-P_RU.pdf
Deye | Hybrid LV 3P | SUN-5K-SG05LP3-EU-SM2 | three-phase | 5000 | 10000 | 800 | 160 | 200 | 650 | 2 | 1+1 | 20 | 30 | 48 | 40-60 | datasheet_local_pdf_verified | Local PDF: SUN-_3-12_K-SG05LP3-EU-SM2_RU.pdf
Deye | Hybrid LV 3P | SUN-6K-SG05LP3-EU-SM2 | three-phase | 6000 | 12000 | 800 | 160 | 200 | 650 | 2 | 1+1 | 20 | 30 | 48 | 40-60 | datasheet_local_pdf_verified | Local PDF: SUN-_3-12_K-SG05LP3-EU-SM2_RU.pdf
Deye | Hybrid LV 3P | SUN-8K-SG05LP3-EU-SM2 | three-phase | 8000 | 16000 | 800 | 160 | 200 | 650 | 2 | 2+2 | 26 | 39 | 48 | 40-60 | datasheet_local_pdf_verified | Local PDF: SUN-_3-12_K-SG05LP3-EU-SM2_RU.pdf
Deye | Hybrid LV 3P | SUN-10K-SG05LP3-EU-SM2 | three-phase | 10000 | 20000 | 800 | 160 | 200 | 650 | 2 | 2+2 | 26 | 39 | 48 | 40-60 | datasheet_local_pdf_verified | Local PDF: SUN-_3-12_K-SG05LP3-EU-SM2_RU.pdf
Deye | Hybrid LV 3P | SUN-12K-SG05LP3-EU-SM2 | three-phase | 12000 | 24000 | 800 | 160 | 200 | 650 | 2 | 2+2 | 26 | 39 | 48 | 40-60 | datasheet_local_pdf_verified | Local PDF: SUN-_3-12_K-SG05LP3-EU-SM2_RU.pdf
Deye | Hybrid LV 3P | SUN-14K-SG05LP3-EU-SM2 | three-phase | 14000 | 28000 | 800 | 160 | 160 | 650 | 2 | 2+2 | 36 | 54 | 48 | 40-60 | datasheet_local_pdf_verified | Local PDF: SUN-_14-20_K-SG05LP3-EU-SM2_RU.pdf
Deye | Hybrid LV 3P | SUN-15K-SG05LP3-EU-SM2 | three-phase | 15000 | 30000 | 800 | 160 | 160 | 650 | 2 | 2+2 | 36 | 54 | 48 | 40-60 | datasheet_local_pdf_verified | Local PDF: SUN-_14-20_K-SG05LP3-EU-SM2_RU.pdf
Deye | Hybrid LV 3P | SUN-16K-SG05LP3-EU-SM2 | three-phase | 16000 | 32000 | 800 | 160 | 160 | 650 | 2 | 2+2 | 36 | 54 | 48 | 40-60 | datasheet_local_pdf_verified | Local PDF: SUN-_14-20_K-SG05LP3-EU-SM2_RU.pdf
Deye | Hybrid LV 3P | SUN-18K-SG05LP3-EU-SM2 | three-phase | 18000 | 36000 | 800 | 160 | 160 | 650 | 2 | 2+2 | 36 | 54 | 48 | 40-60 | datasheet_local_pdf_verified | Local PDF: SUN-_14-20_K-SG05LP3-EU-SM2_RU.pdf
Deye | Hybrid LV 3P | SUN-20K-SG05LP3-EU-SM2 | three-phase | 20000 | 40000 | 800 | 160 | 160 | 650 | 2 | 2+2 | 36 | 54 | 48 | 40-60 | datasheet_local_pdf_verified | Local PDF: SUN-_14-20_K-SG05LP3-EU-SM2_RU.pdf
Deye | Hybrid HV 3P | SUN-10K-SG01HP3-EU-AM2 | three-phase | 10000 | 20000 | 1000 | 180 | 150 | 850 | 2 | 1+1 | 20 | 30 |  | 160-700 | datasheet_local_pdf_verified | Local PDF: SUN-_5-25_K-SG01HP3-EU-AM2_RU.pdf
Deye | Hybrid HV 3P | SUN-12K-SG01HP3-EU-AM2 | three-phase | 12000 | 24000 | 1000 | 180 | 150 | 850 | 2 | 1+1 | 20 | 30 |  | 160-700 | datasheet_local_pdf_verified | Local PDF: SUN-_5-25_K-SG01HP3-EU-AM2_RU.pdf
Deye | Hybrid HV 3P | SUN-15K-SG01HP3-EU-AM2 | three-phase | 15000 | 30000 | 1000 | 180 | 150 | 850 | 2 | 2+2 | 26 | 39 |  | 160-700 | datasheet_local_pdf_verified | Local PDF: SUN-_5-25_K-SG01HP3-EU-AM2_RU.pdf
Deye | Hybrid HV 3P | SUN-20K-SG01HP3-EU-AM2 | three-phase | 20000 | 40000 | 1000 | 180 | 150 | 850 | 2 | 2+2 | 26 | 39 |  | 160-700 | datasheet_local_pdf_verified | Local PDF: SUN-_5-25_K-SG01HP3-EU-AM2_RU.pdf
Deye | Hybrid HV 3P | SUN-25K-SG01HP3-EU-AM2 | three-phase | 25000 | 50000 | 1000 | 180 | 150 | 850 | 2 | 2+1 | 26 | 39 |  | 160-700 | datasheet_local_pdf_verified | Local PDF: SUN-_5-25_K-SG01HP3-EU-AM2_RU.pdf
Deye | Hybrid HV 3P | SUN-30K-SG02HP3-EU-AM3 | three-phase | 30000 | 60000 | 1000 | 180 | 150 | 850 | 3 | 2+2+2 | 36 | 54 |  | 160-700 | datasheet_local_pdf_verified | Local PDF: SUN-_25-30_K-SG02HP3-EU-AM3_RU.pdf
Deye | Hybrid HV 3P | SUN-40K-SG01HP3-EU-BM4 | three-phase | 40000 | 80000 | 1000 | 180 | 150 | 850 | 3 | 2+2+2 | 36 | 55 |  | 160-800 | datasheet_local_pdf_verified | Local PDF: SUN-_29.9-50_K-SG01HP3-EU-BM4_RU.pdf
Deye | Hybrid HV 3P | SUN-50K-SG01HP3-EU-BM4 | three-phase | 50000 | 100000 | 1000 | 180 | 150 | 850 | 4 | 2+2+2+2 | 36 | 55 |  | 160-800 | datasheet_local_pdf_verified | Local PDF: SUN-_29.9-50_K-SG01HP3-EU-BM4_RU.pdf
Deye | Hybrid HV 3P | SUN-60K-SG02HP3-EU-EM6 | three-phase | 60000 | 120000 | 1000 | 180 | 150 | 850 | 6 | 2+2+2+2+2+2 | 36 | 54 |  | 160-1000 | datasheet_local_pdf_verified | Local PDF: SUN-_60-80_K-SG02HP3-EU-EM6_RU.pdf
Deye | Hybrid HV 3P | SUN-70K-SG02HP3-EU-EM6 | three-phase | 70000 | 140000 | 1000 | 180 | 150 | 850 | 6 | 2+2+2+2+2+2 | 36 | 54 |  | 160-1000 | datasheet_local_pdf_verified | Local PDF: SUN-_60-80_K-SG02HP3-EU-EM6_RU.pdf
Deye | Hybrid HV 3P | SUN-75K-SG02HP3-EU-EM6 | three-phase | 75000 | 150000 | 1000 | 180 | 150 | 850 | 6 | 2+2+2+2+2+2 | 36 | 54 |  | 160-1000 | datasheet_local_pdf_verified | Local PDF: SUN-_60-80_K-SG02HP3-EU-EM6_RU.pdf
Deye | Hybrid HV 3P | SUN-80K-SG02HP3-EU-EM6 | three-phase | 80000 | 160000 | 1000 | 180 | 150 | 850 | 6 | 2+2+2+2+2+2 | 36 | 54 |  | 160-1000 | datasheet_local_pdf_verified | Local PDF: SUN-_60-80_K-SG02HP3-EU-EM6_RU.pdf
Deye | Hybrid HV 3P | SUN-100K-SG02HP3-EU-GM10 | three-phase | 100000 | 200000 | 1000 | 180 | 150 | 850 | 10 | 2+2+2+2+2+2+2+2+2+2 | 42 | 63 |  | 160-1000 | datasheet_local_pdf_verified | Local PDF: SUN-_100-125_K-SG02HP3-EU-GM10_RU.pdf
Deye | Hybrid HV 3P | SUN-125K-SG02HP3-EU-GM10 | three-phase | 125000 | 250000 | 1000 | 180 | 150 | 850 | 10 | 2+2+2+2+2+2+2+2+2+2 | 42 | 63 |  | 160-1000 | datasheet_local_pdf_verified | Local PDF: SUN-_100-125_K-SG02HP3-EU-GM10_RU.pdf
Deye | Grid 1P | SUN-1K-G04P1-EU-AM1 | single-phase | 1000 | [11 empty] | model_only_needs_datasheet | Model list provided by user; datasheet parameters pending.
Deye | Grid 1P | SUN-1.5K-G04P1-EU-AM1 | single-phase | 1500 | [11 empty] | model_only_needs_datasheet | Model list provided by user; datasheet parameters pending.
Deye | Grid 1P | SUN-2K-G04P1-EU-AM1 | single-phase | 2000 | [11 empty] | model_only_needs_datasheet | Model list provided by user; datasheet parameters pending.
Deye | Grid 1P | SUN-3K-G04P1-EU-AM1 | single-phase | 3000 | [11 empty] | model_only_needs_datasheet | Model list provided by user; datasheet parameters pending.
Deye | Grid 1P | SUN-3.6K-G04P1-EU-AM1 | single-phase | 3600 | [11 empty] | model_only_needs_datasheet | Model list provided by user; datasheet parameters pending.
Deye | Grid 1P | SUN-4K-G04P1-EU-AM1 | single-phase | 4000 | [11 empty] | model_only_needs_datasheet | Model list provided by user; datasheet parameters pending.
Deye | Grid 1P | SUN-4K-G05P1-EU-AM2 | single-phase | 4000 | 6000 | 550 | 80 | 70 | 500 | 2 | 1+1 | 18 | 27 |  |  | datasheet_local_pdf_verified | Local PDF: SUN-_3.6-6.2_K-G05P1-EU-AM2_RU.pdf
Deye | Grid 1P | SUN-5K-G05P1-EU-AM2 | single-phase | 5000 | 7500 | 550 | 80 | 70 | 500 | 2 | 1+1 | 18 | 27 |  |  | datasheet_local_pdf_verified | Local PDF: SUN-_3.6-6.2_K-G05P1-EU-AM2_RU.pdf
Deye | Grid 1P | SUN-6K-G05P1-EU-AM2 | single-phase | 6000 | 9000 | 550 | 80 | 70 | 500 | 2 | 1+1 | 18 | 27 |  |  | datasheet_local_pdf_verified | Local PDF: SUN-_3.6-6.2_K-G05P1-EU-AM2_RU.pdf
Deye | Grid 1P | SUN-7K-G02P1-EU-AM2 | single-phase | 7000 | 9100 | 550 | 80 | 70 | 500 | 2 | 1+2 | 26 | 39 |  |  | datasheet_local_pdf_verified | Local PDF: SUN-_7-8_K-G02P1-EU-AM2_RU.pdf
Deye | Grid 1P | SUN-7.5K-G02P1-EU-AM2 | single-phase | 7500 | 9800 | 550 | 80 | 70 | 500 | 2 | 1+2 | 26 | 39 |  |  | datasheet_local_pdf_verified | Local PDF: SUN-_7-8_K-G02P1-EU-AM2_RU.pdf
Deye | Grid 1P | SUN-8K-G02P1-EU-AM2 | single-phase | 8000 | 10400 | 550 | 80 | 70 | 500 | 2 | 1+2 | 26 | 39 |  |  | datasheet_local_pdf_verified | Local PDF: SUN-_7-8_K-G02P1-EU-AM2_RU.pdf
Deye | Grid 1P | SUN-9K-G02P1-EU-AM2 | single-phase | 9000 | 13500 | 550 | 80 | 70 | 500 | 2 | 2+2 | 26 | 39 |  |  | datasheet_local_pdf_verified | Local PDF: SUN-_9-10.5_K-G02P1-EU-AM2_RU.pdf
Deye | Grid 1P | SUN-10K-G02P1-EU-AM2 | single-phase | 10000 | 15000 | 550 | 80 | 70 | 500 | 2 | 2+2 | 26 | 39 |  |  | datasheet_local_pdf_verified | Local PDF: SUN-_9-10.5_K-G02P1-EU-AM2_RU.pdf
Deye | Grid 3P | SUN-4K-G06P3-EU-BM2-P1 | three-phase | 4000 | 6000 | 1100 | 140 | 120 | 1000 | 2 | 1+1 | 13 | 19.5 |  |  | datasheet_local_pdf_suffix_review | Local PDF: SUN-_3-15_K-G06P3-EU-BM2_RU.pdf; catalog model suffix is BM2-P1, source PDF suffix is BM2.
Deye | Grid 3P | SUN-5K-G06P3-EU-BM2-P1 | three-phase | 5000 | 7500 | 1100 | 140 | 120 | 1000 | 2 | 1+1 | 13 | 19.5 |  |  | datasheet_local_pdf_suffix_review | Local PDF: SUN-_3-15_K-G06P3-EU-BM2_RU.pdf; catalog model suffix is BM2-P1, source PDF suffix is BM2.
Deye | Grid 3P | SUN-6K-G06P3-EU-BM2-P1 | three-phase | 6000 | 9000 | 1100 | 140 | 120 | 1000 | 2 | 1+1 | 13 | 19.5 |  |  | datasheet_local_pdf_suffix_review | Local PDF: SUN-_3-15_K-G06P3-EU-BM2_RU.pdf; catalog model suffix is BM2-P1, source PDF suffix is BM2.
Deye | Grid 3P | SUN-7K-G06P3-EU-BM2-P1 | three-phase | 7000 | 10500 | 1100 | 140 | 120 | 1000 | 2 | 1+1 | 13 | 19.5 |  |  | datasheet_local_pdf_suffix_review | Local PDF: SUN-_3-15_K-G06P3-EU-BM2_RU.pdf; catalog model suffix is BM2-P1, source PDF suffix is BM2.
Deye | Grid 3P | SUN-8K-G06P3-EU-BM2-P1 | three-phase | 8000 | 12000 | 1100 | 140 | 120 | 1000 | 2 | 1+1 | 13 | 19.5 |  |  | datasheet_local_pdf_suffix_review | Local PDF: SUN-_3-15_K-G06P3-EU-BM2_RU.pdf; catalog model suffix is BM2-P1, source PDF suffix is BM2.
Deye | Grid 3P | SUN-9K-G06P3-EU-BM2-P1 | three-phase | 9000 | 13500 | 1100 | 140 | 120 | 1000 | 2 | 1+1 | 13 | 19.5 |  |  | datasheet_local_pdf_suffix_review | Local PDF: SUN-_3-15_K-G06P3-EU-BM2_RU.pdf; catalog model suffix is BM2-P1, source PDF suffix is BM2.
Deye | Grid 3P | SUN-10K-G06P3-EU-BM2-P1 | three-phase | 10000 | 15000 | 1100 | 140 | 120 | 1000 | 2 | 1+1 | 13 | 19.5 |  |  | datasheet_local_pdf_suffix_review | Local PDF: SUN-_3-15_K-G06P3-EU-BM2_RU.pdf; catalog model suffix is BM2-P1, source PDF suffix is BM2.
Deye | Grid 3P | SUN-12K-G06P3-EU-BM2-P1 | three-phase | 12000 | 18000 | 1100 | 140 | 120 | 1000 | 2 | 1+1 | 13 | 19.5 |  |  | datasheet_local_pdf_suffix_review | Local PDF: SUN-_3-15_K-G06P3-EU-BM2_RU.pdf; catalog model suffix is BM2-P1, source PDF suffix is BM2.
Deye | Grid 3P | SUN-15K-G06P3-EU-BM2-P1 | three-phase | 15000 | 22500 | 1100 | 140 | 120 | 1000 | 2 | 1+2 | 26 | 39 |  |  | datasheet_local_pdf_suffix_review | Local PDF: SUN-_3-15_K-G06P3-EU-BM2_RU.pdf; catalog model suffix is BM2-P1, source PDF suffix is BM2.
Deye | Grid 3P | SUN-18K-G05 | three-phase | 18000 | 23400 | 1100 | 250 | 200 | 1000 | 2 | 2+2 | 26 | 39 |  |  | datasheet_local_pdf_verified | Local PDF: SUN-_18-25_K-G05P3-EU-CM2_RU.pdf
Deye | Grid 3P | SUN-20K-G05 | three-phase | 20000 | 26000 | 1100 | 250 | 200 | 1000 | 2 | 2+2 | 26 | 39 |  |  | datasheet_local_pdf_verified | Local PDF: SUN-_18-25_K-G05P3-EU-CM2_RU.pdf
Deye | Grid 3P | SUN-25K-G05 | three-phase | 25000 | 32500 | 1100 | 250 | 200 | 1000 | 2 | 2+2 | 26 | 39 |  |  | datasheet_local_pdf_verified | Local PDF: SUN-_18-25_K-G05P3-EU-CM2_RU.pdf
Deye | Grid 3P | SUN-30K-G04 | three-phase | 30000 | 39000 | 1100 | 250 | 200 | 1000 | 2 | 3+3 | 40 | 60 |  |  | datasheet_local_pdf_verified | Local PDF: SUN-_30-36_K-G04P3-EU-CM2_RU.pdf
Deye | Grid 3P | SUN-33K-G04 | three-phase | 33000 | 42900 | 1100 | 250 | 200 | 1000 | 2 | 3+3 | 40 | 60 |  |  | datasheet_local_pdf_verified | Local PDF: SUN-_30-36_K-G04P3-EU-CM2_RU.pdf
Deye | Grid 3P | SUN-35K-G04 | three-phase | 35000 | 45500 | 1100 | 250 | 200 | 1000 | 2 | 3+3 | 40 | 60 |  |  | datasheet_local_pdf_verified | Local PDF: SUN-_30-36_K-G04P3-EU-CM2_RU.pdf
Deye | Grid 3P | SUN-40K-G04 | three-phase | 40000 | 60000 | 1100 | 250 | 200 | 1000 | 3 | 3+3+3 | 40 | 60 |  |  | datasheet_local_pdf_verified | Local PDF: SUN-_40-50_K-G04P3-EU-CM4_RU.pdf
Deye | Grid 3P | SUN-45K-G04 | three-phase | 45000 | 67500 | 1100 | 250 | 200 | 1000 | 3 | 3+3+3 | 40 | 60 |  |  | datasheet_local_pdf_verified | Local PDF: SUN-_40-50_K-G04P3-EU-CM4_RU.pdf
Deye | Grid 3P | SUN-50K-G04 | three-phase | 50000 | 75000 | 1100 | 250 | 200 | 1000 | 4 | 3+3+3+3 | 40 | 60 |  |  | datasheet_local_pdf_verified | Local PDF: SUN-_40-50_K-G04P3-EU-CM4_RU.pdf
Deye | Grid 3P | SUN-60K-G04P3-EU-AM4 | three-phase | 60000 | 90000 | 1100 | 250 | 200 | 1000 | 4 | 4+4+4+4 | 40 | 60 |  |  | datasheet_local_pdf_verified | Local PDF: SUN-_60-80_K-G04P3-EU-AM4_RU.pdf
Deye | Grid 3P | SUN-70K-G04P3-EU-AM4 | three-phase | 70000 | 105000 | 1100 | 250 | 200 | 1000 | 4 | 4+4+4+4 | 40 | 60 |  |  | datasheet_local_pdf_verified | Local PDF: SUN-_60-80_K-G04P3-EU-AM4_RU.pdf
Deye | Grid 3P | SUN-75K-G04P3-EU-AM4 | three-phase | 75000 | 112500 | 1100 | 250 | 200 | 1000 | 4 | 4+4+4+4 | 40 | 60 |  |  | datasheet_local_pdf_verified | Local PDF: SUN-_60-80_K-G04P3-EU-AM4_RU.pdf
Deye | Grid 3P | SUN-80K-G04P3-EU-AM4 | three-phase | 80000 | 120000 | 1100 | 250 | 200 | 1000 | 4 | 4+4+4+4 | 40 | 60 |  |  | datasheet_local_pdf_verified | Local PDF: SUN-_60-80_K-G04P3-EU-AM4_RU.pdf
Deye | Grid 3P | SUN-100K-G03 | three-phase | 100000 | [11 empty] | model_only_needs_datasheet | Model list provided by user; datasheet parameters pending.
Deye | Grid 3P | SUN-110K-G03 | three-phase | 110000 | [11 empty] | model_only_needs_datasheet | Model list provided by user; datasheet parameters pending.
Deye | Grid 3P | SUN-120K-G01P3-EU-AM8 | three-phase | 120000 | [11 empty] | model_only_needs_datasheet | Model list provided by user; datasheet parameters pending.
Deye | Grid 3P | SUN-125K-G01P3-EU-AM8 | three-phase | 125000 | [11 empty] | model_only_needs_datasheet | Model list provided by user; datasheet parameters pending.
Deye | Grid 3P | SUN-130K-G01P3-EU-AM8 | three-phase | 130000 | [11 empty] | model_only_needs_datasheet | Model list provided by user; datasheet parameters pending.
Deye | Grid 3P | SUN-135K-G01P3-EU-AM8 | three-phase | 135000 | [11 empty] | model_only_needs_datasheet | Model list provided by user; datasheet parameters pending.
Deye | Grid 3P | SUN-136K-G01P3-EU-AM8 | three-phase | 136000 | [11 empty] | model_only_needs_datasheet | Model list provided by user; datasheet parameters pending.
Deye | LV Hybrid | SUN-3.6K-SG03LP1-EU | single-phase | 3600 | 4680 | 500 | 150 | 125 | 425 | 2 | 1+1 | 13 | 17 | 48 | 40-60 | seed_verify_datasheet | Starter record for low-voltage hybrid inverter calculations.
Deye | LV Hybrid | SUN-5K-SG03LP1-EU | single-phase | 5000 | 6500 | 500 | 150 | 125 | 425 | 2 | 1+1 | 13 | 17 | 48 | 40-60 | seed_verify_datasheet | Starter record for low-voltage hybrid inverter calculations.
Deye | LV Hybrid | SUN-6K-SG03LP1-EU | single-phase | 6000 | 7800 | 500 | 150 | 125 | 425 | 2 | 1+1 | 13 | 17 | 48 | 40-60 | seed_verify_datasheet | Starter record for low-voltage hybrid inverter calculations.
Deye | LV Hybrid | SUN-8K-SG01LP1-EU | single-phase | 8000 | 10400 | 500 | 150 | 125 | 425 | 2 | 2+2 | 26 | 34 | 48 | 40-60 | seed_verify_datasheet | Starter record; verify exact PV current and string inputs for selected market version.
Growatt | SPH TL BL-UP | SPH 3000TL BL-UP | single-phase | 3000 | [11 empty] | model_only_needs_datasheet | Hybrid/storage inverter model candidate; datasheet parameters pending.
Growatt | SPH TL BL-UP | SPH 3600TL BL-UP | single-phase | 3600 | [11 empty] | model_only_needs_datasheet | Hybrid/storage inverter model candidate; datasheet parameters pending.
Growatt | SPH TL BL-UP | SPH 4000TL BL-UP | single-phase | 4000 | [11 empty] | model_only_needs_datasheet | Hybrid/storage inverter model candidate; datasheet parameters pending.
Growatt | SPH TL BL-UP | SPH 4600TL BL-UP | single-phase | 4600 | [11 empty] | model_only_needs_datasheet | Hybrid/storage inverter model candidate; datasheet parameters pending.
Growatt | SPH TL BL-UP | SPH 5000TL BL-UP | single-phase | 5000 | [11 empty] | model_only_needs_datasheet | Hybrid/storage inverter model candidate; datasheet parameters pending.
Growatt | SPH TL BL-UP | SPH 6000TL BL-UP | single-phase | 6000 | [11 empty] | model_only_needs_datasheet | Hybrid/storage inverter model candidate; datasheet parameters pending.
Growatt | SPH TL3 BH-UP | SPH 4000TL3 BH-UP | three-phase | 4000 | [11 empty] | model_only_needs_datasheet | Hybrid/storage inverter model candidate; datasheet parameters pending.
Growatt | SPH TL3 BH-UP | SPH 5000TL3 BH-UP | three-phase | 5000 | [11 empty] | model_only_needs_datasheet | Hybrid/storage inverter model candidate; datasheet parameters pending.
Growatt | SPH TL3 BH-UP | SPH 6000TL3 BH-UP | three-phase | 6000 | [11 empty] | model_only_needs_datasheet | Hybrid/storage inverter model candidate; datasheet parameters pending.
Growatt | SPH TL3 BH-UP | SPH 7000TL3 BH-UP | three-phase | 7000 | [11 empty] | model_only_needs_datasheet | Hybrid/storage inverter model candidate; datasheet parameters pending.
Growatt | SPH TL3 BH-UP | SPH 8000TL3 BH-UP | three-phase | 8000 | [11 empty] | model_only_needs_datasheet | Hybrid/storage inverter model candidate; datasheet parameters pending.
Growatt | SPH TL3 BH-UP | SPH 10000TL3 BH-UP | three-phase | 10000 | [11 empty] | model_only_needs_datasheet | Hybrid/storage inverter model candidate; datasheet parameters pending.
Growatt | MIN TL-XH | MIN 2500TL-XH | single-phase | 2500 | [11 empty] | model_only_needs_datasheet | Battery-ready inverter model candidate; datasheet parameters pending.
Growatt | MIN TL-XH | MIN 3000TL-XH | single-phase | 3000 | [11 empty] | model_only_needs_datasheet | Battery-ready inverter model candidate; datasheet parameters pending.
Growatt | MIN TL-XH | MIN 3600TL-XH | single-phase | 3600 | [11 empty] | model_only_needs_datasheet | Battery-ready inverter model candidate; datasheet parameters pending.
Growatt | MIN TL-XH | MIN 4200TL-XH | single-phase | 4200 | [11 empty] | model_only_needs_datasheet | Battery-ready inverter model candidate; datasheet parameters pending.
Growatt | MIN TL-XH | MIN 4600TL-XH | single-phase | 4600 | [11 empty] | model_only_needs_datasheet | Battery-ready inverter model candidate; datasheet parameters pending.
Growatt | MIN TL-XH | MIN 5000TL-XH | single-phase | 5000 | [11 empty] | model_only_needs_datasheet | Battery-ready inverter model candidate; datasheet parameters pending.
Growatt | MIN TL-XH | MIN 6000TL-XH | single-phase | 6000 | [11 empty] | model_only_needs_datasheet | Battery-ready inverter model candidate; datasheet parameters pending.
Growatt | MOD TL3-XH BP | MOD 3000TL3-XH BP | three-phase | 3000 | [11 empty] | model_only_needs_datasheet | Battery-ready inverter model candidate; datasheet parameters pending.
Growatt | MOD TL3-XH BP | MOD 4000TL3-XH BP | three-phase | 4000 | [11 empty] | model_only_needs_datasheet | Battery-ready inverter model candidate; datasheet parameters pending.
Growatt | MOD TL3-XH BP | MOD 5000TL3-XH BP | three-phase | 5000 | [11 empty] | model_only_needs_datasheet | Battery-ready inverter model candidate; datasheet parameters pending.
Growatt | MOD TL3-XH BP | MOD 6000TL3-XH BP | three-phase | 6000 | [11 empty] | model_only_needs_datasheet | Battery-ready inverter model candidate; datasheet parameters pending.
Growatt | MOD TL3-XH BP | MOD 7000TL3-XH BP | three-phase | 7000 | [11 empty] | model_only_needs_datasheet | Battery-ready inverter model candidate; datasheet parameters pending.
Growatt | MOD TL3-XH BP | MOD 8000TL3-XH BP | three-phase | 8000 | [11 empty] | model_only_needs_datasheet | Battery-ready inverter model candidate; datasheet parameters pending.
Growatt | MOD TL3-XH BP | MOD 9000TL3-XH BP | three-phase | 9000 | [11 empty] | model_only_needs_datasheet | Battery-ready inverter model candidate; datasheet parameters pending.
Growatt | MOD TL3-XH BP | MOD 10KTL3-XH BP | three-phase | 10000 | [11 empty] | model_only_needs_datasheet | Battery-ready inverter model candidate; datasheet parameters pending.
Growatt | MOD TL3-XH BP | MOD 11KTL3-XH BP | three-phase | 11000 | [11 empty] | model_only_needs_datasheet | Battery-ready inverter model candidate; datasheet parameters pending.
Growatt | MOD TL3-XH BP | MOD 12KTL3-XH BP | three-phase | 12000 | [11 empty] | model_only_needs_datasheet | Battery-ready inverter model candidate; datasheet parameters pending.
Growatt | MOD TL3-XH BP | MOD 13KTL3-XH BP | three-phase | 13000 | [11 empty] | model_only_needs_datasheet | Battery-ready inverter model candidate; datasheet parameters pending.
Growatt | MOD TL3-XH BP | MOD 15KTL3-XH BP | three-phase | 15000 | [11 empty] | model_only_needs_datasheet | Battery-ready inverter model candidate; datasheet parameters pending.
Growatt | WIT TL3-A-LV | WIT 50KTL3-A-LV | three-phase | 50000 | [11 empty] | model_only_needs_datasheet | Commercial hybrid/storage inverter model candidate; datasheet parameters pending.
Growatt | WIT TL3-A-LV | WIT 63KTL3-A-LV | three-phase | 63000 | [11 empty] | model_only_needs_datasheet | Commercial hybrid/storage inverter model candidate; datasheet parameters pending.
Growatt | WIT TL3-A-LV | WIT 75KTL3-A-LV | three-phase | 75000 | [11 empty] | model_only_needs_datasheet | Commercial hybrid/storage inverter model candidate; datasheet parameters pending.
Growatt | WIT TL3-A-LV | WIT 100KTL3-A-LV | three-phase | 100000 | [11 empty] | model_only_needs_datasheet | Commercial hybrid/storage inverter model candidate; datasheet parameters pending.
MUST | PV1800 VHM | PV1800 VHM-2KW-24V | single-phase | 2000 | [9 empty] | 24 |  | model_only_needs_datasheet | Hybrid inverter model candidate; datasheet parameters pending.
MUST | PV1800 VHM | PV1800 VHM-3KW-24V | single-phase | 3000 | [9 empty] | 24 |  | model_only_needs_datasheet | Hybrid inverter model candidate; datasheet parameters pending.
MUST | PV1800 VHM | PV1800 VHM-4KW-48V | single-phase | 4000 | [9 empty] | 48 |  | model_only_needs_datasheet | Hybrid inverter model candidate; datasheet parameters pending.
MUST | PV1800 VHM | PV1800 VHM-5KW-48V | single-phase | 5000 | [9 empty] | 48 |  | model_only_needs_datasheet | Hybrid inverter model candidate; datasheet parameters pending.
MUST | PV1800 PRO | PV1800 PRO-3KW-24V | single-phase | 3000 | [9 empty] | 24 |  | model_only_needs_datasheet | Hybrid inverter model candidate; datasheet parameters pending.
MUST | PV1800 PRO | PV1800 PRO-5.2KW-48V | single-phase | 5200 | [9 empty] | 48 |  | model_only_needs_datasheet | Hybrid inverter model candidate; datasheet parameters pending.
MUST | PV1800 PRO | PV1800 PRO-6.2KW-48V | single-phase | 6200 | [9 empty] | 48 |  | model_only_needs_datasheet | Hybrid inverter model candidate; datasheet parameters pending.
MUST | PV18 VPM | PV18-3024 VPM | single-phase | 3000 | [9 empty] | 24 |  | model_only_needs_datasheet | Hybrid inverter model candidate; datasheet parameters pending.
MUST | PV18 VPM | PV18-5048 VPM | single-phase | 5000 | [9 empty] | 48 |  | model_only_needs_datasheet | Hybrid inverter model candidate; datasheet parameters pending.
MUST | PV18 VPM | PV18-5548 VPM | single-phase | 5500 | [9 empty] | 48 |  | model_only_needs_datasheet | Hybrid inverter model candidate; datasheet parameters pending.
MUST | PV18 VPM | PV18-6048 VPM | single-phase | 6000 | [9 empty] | 48 |  | model_only_needs_datasheet | Hybrid inverter model candidate; datasheet parameters pending.
MUST | PV18 VHM | PV18-3024 VHM | single-phase | 3000 | [9 empty] | 24 |  | model_only_needs_datasheet | Hybrid inverter model candidate; datasheet parameters pending.
MUST | PV18 VHM | PV18-5048 VHM | single-phase | 5000 | [9 empty] | 48 |  | model_only_needs_datasheet | Hybrid inverter model candidate; datasheet parameters pending.
MUST | PV18 VHM | PV18-5548 VHM | single-phase | 5500 | [9 empty] | 48 |  | model_only_needs_datasheet | Hybrid inverter model candidate; datasheet parameters pending.
MUST | PV19 VPM | PV19-3024 VPM | single-phase | 3000 | [9 empty] | 24 |  | model_only_needs_datasheet | Hybrid inverter model candidate; datasheet parameters pending.
MUST | PV19 VPM | PV19-5048 VPM | single-phase | 5000 | [9 empty] | 48 |  | model_only_needs_datasheet | Hybrid inverter model candidate; datasheet parameters pending.
MUST | PV19 VPM | PV19-6048 VPM | single-phase | 6000 | [9 empty] | 48 |  | model_only_needs_datasheet | Hybrid inverter model candidate; datasheet parameters pending.
MUST | PH1800 PLUS | PH1800 PLUS-5.5KW-48V | single-phase | 5500 | [9 empty] | 48 |  | model_only_needs_datasheet | Hybrid inverter model candidate; datasheet parameters pending.
PowMr | POW-HVM | POW-HVM3.0KW-24V | single-phase | 3000 | [9 empty] | 24 |  | model_only_needs_datasheet | Model found in PowMr official catalog/manual references; datasheet parameters pending.
PowMr | POW-HVM | POW-HVM5.5K-48V | single-phase | 5500 | [9 empty] | 48 |  | model_only_needs_datasheet | Model found in PowMr official catalog/manual references; datasheet parameters pending.
PowMr | POW-HVM | POW-HVM5.5K-48V-LIP | single-phase | 5500 | [9 empty] | 48 |  | model_only_needs_datasheet | Model found in PowMr official catalog/manual references; datasheet parameters pending.
PowMr | POW-HVM | POW-HVM5.5M | single-phase | 5500 | [11 empty] | model_only_needs_datasheet | Model found in PowMr official catalog/manual references; datasheet parameters pending.
PowMr | POW-HPM | POW-HPM5.6KW | single-phase | 5600 | [11 empty] | model_only_needs_datasheet | Model found in PowMr official catalog/manual references; datasheet parameters pending.
PowMr | POW-SunSmart | POW-SUNSMART-5.5KW-48V | single-phase | 5500 | [9 empty] | 48 |  | model_only_needs_datasheet | Model found in PowMr official catalog/manual references; datasheet parameters pending.
PowMr | POW-SunSmart | POW-SUNSMART-5.6KW-48V | single-phase | 5600 | [9 empty] | 48 |  | model_only_needs_datasheet | Model found in PowMr official catalog/manual references; datasheet parameters pending.
PowMr | POW-VM | POW-VM5K-III | single-phase | 5000 | [11 empty] | model_only_needs_datasheet | Model found in PowMr official catalog/manual references; datasheet parameters pending.
PowMr | POW-MAX | POW-MAX-8KW | single-phase | 8000 | [11 empty] | model_only_needs_datasheet | Model found in PowMr official catalog/manual references; datasheet parameters pending.
PowMr | POW-SunSmart LVM | POW-SunSmart LVM12K | split-phase | 12000 | [9 empty] | 48 |  | model_only_needs_datasheet | Model found in PowMr official 110V hybrid inverter catalog; datasheet parameters pending.
PowMr | SOLXPOW X3 | SOLXPOW X3-12K | three-phase | 12000 | [11 empty] | model_only_needs_datasheet | Model found in PowMr official 220V hybrid inverter catalog; datasheet parameters pending.
PowMr | SOLXPOW X3 | SOLXPOW X3-20K | three-phase | 20000 | [11 empty] | model_only_needs_datasheet | Model found in PowMr official 220V hybrid inverter catalog; datasheet parameters pending.
PowMr | SOLXPOW X4 | SOLXPOW X4-50K | three-phase | 50000 | [11 empty] | model_only_needs_datasheet | Model found in PowMr official 220V hybrid inverter catalog; datasheet parameters pending.
Solis | RHI 1P | RHI-3K-48ES-5G | single-phase | 3000 | [9 empty] | 48 |  | model_only_needs_datasheet | Hybrid inverter model candidate; datasheet parameters pending.
Solis | RHI 1P | RHI-3.6K-48ES-5G | single-phase | 3600 | [9 empty] | 48 |  | model_only_needs_datasheet | Hybrid inverter model candidate; datasheet parameters pending.
Solis | RHI 1P | RHI-4.6K-48ES-5G | single-phase | 4600 | [9 empty] | 48 |  | model_only_needs_datasheet | Hybrid inverter model candidate; datasheet parameters pending.
Solis | RHI 1P | RHI-5K-48ES-5G | single-phase | 5000 | [9 empty] | 48 |  | model_only_needs_datasheet | Hybrid inverter model candidate; datasheet parameters pending.
Solis | RHI 1P | RHI-6K-48ES-5G | single-phase | 6000 | [9 empty] | 48 |  | model_only_needs_datasheet | Hybrid inverter model candidate; datasheet parameters pending.
Solis | S5 EH1P | S5-EH1P3K-L | single-phase | 3000 | [11 empty] | model_only_needs_datasheet | Hybrid inverter model candidate; datasheet parameters pending.
Solis | S5 EH1P | S5-EH1P3.6K-L | single-phase | 3600 | [11 empty] | model_only_needs_datasheet | Hybrid inverter model candidate; datasheet parameters pending.
Solis | S5 EH1P | S5-EH1P4.6K-L | single-phase | 4600 | [11 empty] | model_only_needs_datasheet | Hybrid inverter model candidate; datasheet parameters pending.
Solis | S5 EH1P | S5-EH1P5K-L | single-phase | 5000 | [11 empty] | model_only_needs_datasheet | Hybrid inverter model candidate; datasheet parameters pending.
Solis | S5 EH1P | S5-EH1P6K-L | single-phase | 6000 | [11 empty] | model_only_needs_datasheet | Hybrid inverter model candidate; datasheet parameters pending.
Solis | S6 EH1P | S6-EH1P3K-L-EU | single-phase | 3000 | [11 empty] | model_only_needs_datasheet | Hybrid inverter model candidate; datasheet parameters pending.
Solis | S6 EH1P | S6-EH1P3.6K-L-EU | single-phase | 3600 | [11 empty] | model_only_needs_datasheet | Hybrid inverter model candidate; datasheet parameters pending.
Solis | S6 EH1P | S6-EH1P4.6K-L-EU | single-phase | 4600 | [11 empty] | model_only_needs_datasheet | Hybrid inverter model candidate; datasheet parameters pending.
Solis | S6 EH1P | S6-EH1P5K-L-EU | single-phase | 5000 | [11 empty] | model_only_needs_datasheet | Hybrid inverter model candidate; datasheet parameters pending.
Solis | S6 EH1P | S6-EH1P6K-L-EU | single-phase | 6000 | [11 empty] | model_only_needs_datasheet | Hybrid inverter model candidate; datasheet parameters pending.
Solis | S6 EH1P | S6-EH1P8K-L-PRO | single-phase | 8000 | [11 empty] | model_only_needs_datasheet | Hybrid inverter model candidate; datasheet parameters pending.
Solis | S6 EH1P | S6-EH1P10K-L-PRO | single-phase | 10000 | [11 empty] | model_only_needs_datasheet | Hybrid inverter model candidate; datasheet parameters pending.
Solis | S6 EH3P | S6-EH3P5K-H-EU | three-phase | 5000 | [11 empty] | model_only_needs_datasheet | Hybrid inverter model candidate; datasheet parameters pending.
Solis | S6 EH3P | S6-EH3P6K-H-EU | three-phase | 6000 | [11 empty] | model_only_needs_datasheet | Hybrid inverter model candidate; datasheet parameters pending.
Solis | S6 EH3P | S6-EH3P8K-H-EU | three-phase | 8000 | [11 empty] | model_only_needs_datasheet | Hybrid inverter model candidate; datasheet parameters pending.
Solis | S6 EH3P | S6-EH3P10K-H-EU | three-phase | 10000 | [11 empty] | model_only_needs_datasheet | Hybrid inverter model candidate; datasheet parameters pending.
Solis | S6 EH3P | S6-EH3P12K-H-EU | three-phase | 12000 | [11 empty] | model_only_needs_datasheet | Hybrid inverter model candidate; datasheet parameters pending.
Solis | S6 EH3P | S6-EH3P15K-H-EU | three-phase | 15000 | [11 empty] | model_only_needs_datasheet | Hybrid inverter model candidate; datasheet parameters pending.
Solis | S6 EH3P | S6-EH3P20K-H-EU | three-phase | 20000 | [11 empty] | model_only_needs_datasheet | Hybrid inverter model candidate; datasheet parameters pending.
Solis | S6 EH3P | S6-EH3P29.9K-H | three-phase | 29900 | [11 empty] | model_only_needs_datasheet | Hybrid inverter model candidate; datasheet parameters pending.
Solis | S6 EH3P | S6-EH3P30K-H | three-phase | 30000 | [11 empty] | model_only_needs_datasheet | Hybrid inverter model candidate; datasheet parameters pending.
Solis | S6 EH3P | S6-EH3P40K-H | three-phase | 40000 | [11 empty] | model_only_needs_datasheet | Hybrid inverter model candidate; datasheet parameters pending.
Solis | S6 EH3P | S6-EH3P50K-H | three-phase | 50000 | [11 empty] | model_only_needs_datasheet | Hybrid inverter model candidate; datasheet parameters pending.

## Panels
brand | series | model | power_stc_w | vmp_stc_v | imp_stc_a | voc_stc_v | isc_stc_a | temp_coeff_pmax_pct_c | temp_coeff_voc_pct_c | temp_coeff_isc_pct_c | module_length_mm | module_width_mm | module_depth_mm | data_status | notes
Astronergy | ASTRO N5 | CHSM54N-HC-430 | 430 | [10 empty] | model_only_needs_datasheet | Panel catalog model; datasheet parameters pending.
Astronergy | ASTRO N5 | CHSM54N-HC-435 | 435 | [10 empty] | model_only_needs_datasheet | Panel catalog model; datasheet parameters pending.
Astronergy | ASTRO N5 | CHSM54N-HC-440 | 440 | [10 empty] | model_only_needs_datasheet | Panel catalog model; datasheet parameters pending.
Astronergy | ASTRO N7 | CHSM72N(DG)/F-BH-570 | 570 | [10 empty] | model_only_needs_datasheet | Panel catalog model; datasheet parameters pending.
Astronergy | ASTRO N7 | CHSM72N(DG)/F-BH-575 | 575 | [10 empty] | model_only_needs_datasheet | Panel catalog model; datasheet parameters pending.
Astronergy | ASTRO N7 | CHSM72N(DG)/F-BH-580 | 580 | [10 empty] | model_only_needs_datasheet | Panel catalog model; datasheet parameters pending.
Astronergy | ASTRO N7 | CHSM66N(DG)/F-BH-615 | 615 | [10 empty] | model_only_needs_datasheet | Panel catalog model; datasheet parameters pending.
Astronergy | ASTRO N7 | CHSM66N(DG)/F-BH-620 | 620 | [10 empty] | model_only_needs_datasheet | Panel catalog model; datasheet parameters pending.
JA Solar | DeepBlue 3.0 | JAM54S30-410/MR | 410 | [10 empty] | model_only_needs_datasheet | Panel catalog model; datasheet parameters pending.
JA Solar | DeepBlue 3.0 | JAM54S30-415/MR | 415 | [10 empty] | model_only_needs_datasheet | Panel catalog model; datasheet parameters pending.
JA Solar | DeepBlue 3.0 | JAM54S30-420/MR | 420 | [10 empty] | model_only_needs_datasheet | Panel catalog model; datasheet parameters pending.
JA Solar | DeepBlue 3.0 Pro | JAM54D40-440/LB | 440 | [10 empty] | model_only_needs_datasheet | Panel catalog model; datasheet parameters pending.
JA Solar | DeepBlue 3.0 Pro | JAM54D40-445/LB | 445 | [10 empty] | model_only_needs_datasheet | Panel catalog model; datasheet parameters pending.
JA Solar | DeepBlue 4.0 Pro | JAM72D42-575/LB | 575 | [10 empty] | model_only_needs_datasheet | Panel catalog model; datasheet parameters pending.
JA Solar | DeepBlue 4.0 Pro | JAM72D42-580/LB | 580 | [10 empty] | model_only_needs_datasheet | Panel catalog model; datasheet parameters pending.
JA Solar | DeepBlue 4.0 Pro | JAM72D42-585/LB | 585 | [10 empty] | model_only_needs_datasheet | Panel catalog model; datasheet parameters pending.
JA Solar | DeepBlue 4.0 Pro | JAM72D42-590/LB | 590 | [10 empty] | model_only_needs_datasheet | Panel catalog model; datasheet parameters pending.
JA Solar | DeepBlue 4.0 Pro | JAM72D42-595/LB | 595 | [10 empty] | model_only_needs_datasheet | Panel catalog model; datasheet parameters pending.
Jinko | Tiger Neo N-type 54HL4R | JKM420N-54HL4R-B | 420 | [10 empty] | model_only_needs_datasheet | Panel catalog model; datasheet parameters pending.
Jinko | Tiger Neo N-type 54HL4R | JKM425N-54HL4R-B | 425 | [10 empty] | model_only_needs_datasheet | Panel catalog model; datasheet parameters pending.
Jinko | Tiger Neo N-type 54HL4R | JKM430N-54HL4R-B | 430 | [10 empty] | model_only_needs_datasheet | Panel catalog model; datasheet parameters pending.
Jinko | Tiger Neo N-type 60HL4 | JKM465N-60HL4-V | 465 | [10 empty] | model_only_needs_datasheet | Panel catalog model; datasheet parameters pending.
Jinko | Tiger Neo N-type 60HL4 | JKM470N-60HL4-V | 470 | [10 empty] | model_only_needs_datasheet | Panel catalog model; datasheet parameters pending.
Jinko | Tiger Neo N-type 60HL4 | JKM475N-60HL4-V | 475 | [10 empty] | model_only_needs_datasheet | Panel catalog model; datasheet parameters pending.
Jinko | Tiger Neo N-type 66HL4M | JKM610N-66HL4M-V | 610 | [10 empty] | model_only_needs_datasheet | Panel catalog model; datasheet parameters pending.
Jinko | Tiger Neo N-type 66HL4M | JKM615N-66HL4M-V | 615 | [10 empty] | model_only_needs_datasheet | Panel catalog model; datasheet parameters pending.
Jinko | Tiger Neo N-type 66HL4M | JKM620N-66HL4M-V | 620 | [10 empty] | model_only_needs_datasheet | Panel catalog model; datasheet parameters pending.
Jinko | Tiger Neo N-type 72HL4 | JKM565N-72HL4-V | 565 | 43.28 | 13.06 | 51.7 | 13.86 | -0.29 | -0.25 | 0.045 | 2278 | 1134 | 30 | seed_verify_datasheet | Starter record for string sizing tests.
Jinko | Tiger Neo N-type 72HL4 | JKM570N-72HL4-V | 570 | 43.52 | 13.1 | 51.89 | 13.89 | -0.29 | -0.25 | 0.045 | 2278 | 1134 | 30 | seed_verify_datasheet | Starter record for string sizing tests.
Jinko | Tiger Neo N-type 72HL4 | JKM575N-72HL4-V | 575 | 43.76 | 13.14 | 52.08 | 13.92 | -0.29 | -0.25 | 0.045 | 2278 | 1134 | 30 | seed_verify_datasheet | Starter record for string sizing tests.
Jinko | Tiger Neo N-type 72HL4 | JKM580N-72HL4-V | 580 | 43.99 | 13.19 | 52.27 | 13.96 | -0.29 | -0.25 | 0.045 | 2278 | 1134 | 30 | seed_verify_datasheet | Starter record for string sizing tests.
Jinko | Tiger Neo N-type 72HL4 | JKM585N-72HL4-V | 585 | 44.23 | 13.23 | 52.46 | 14 | -0.29 | -0.25 | 0.045 | 2278 | 1134 | 30 | seed_verify_datasheet | Starter record for string sizing tests.
LONGi | Hi-MO 6 Explorer | LR5-54HTH-425M | 425 | [10 empty] | model_only_needs_datasheet | Panel catalog model; datasheet parameters pending.
LONGi | Hi-MO 6 Explorer | LR5-54HTH-430M | 430 | [10 empty] | model_only_needs_datasheet | Panel catalog model; datasheet parameters pending.
LONGi | Hi-MO 6 Explorer | LR5-54HTH-435M | 435 | [10 empty] | model_only_needs_datasheet | Panel catalog model; datasheet parameters pending.
LONGi | Hi-MO 7 | LR5-72HGD-585M | 585 | [10 empty] | model_only_needs_datasheet | Panel catalog model; datasheet parameters pending.
LONGi | Hi-MO 7 | LR5-72HGD-590M | 590 | [10 empty] | model_only_needs_datasheet | Panel catalog model; datasheet parameters pending.
LONGi | Hi-MO 7 | LR5-72HGD-595M | 595 | [10 empty] | model_only_needs_datasheet | Panel catalog model; datasheet parameters pending.
LONGi | Hi-MO X6 | LR5-54HTB-430M | 430 | [10 empty] | model_only_needs_datasheet | Panel catalog model; datasheet parameters pending.
LONGi | Hi-MO X6 | LR5-54HTB-435M | 435 | [10 empty] | model_only_needs_datasheet | Panel catalog model; datasheet parameters pending.
LONGi | Hi-MO 6 | LR5-72HTH-565M | 565 | 42.94 | 13.16 | 51.21 | 14.01 | -0.29 | -0.23 | 0.05 | 2278 | 1134 | 35 | seed_verify_datasheet | Starter record for string sizing tests.
LONGi | Hi-MO 6 | LR5-72HTH-570M | 570 | 43.13 | 13.22 | 51.4 | 14.07 | -0.29 | -0.23 | 0.05 | 2278 | 1134 | 35 | seed_verify_datasheet | Starter record for string sizing tests.
LONGi | Hi-MO 6 | LR5-72HTH-575M | 575 | 43.32 | 13.28 | 51.59 | 14.14 | -0.29 | -0.23 | 0.05 | 2278 | 1134 | 35 | seed_verify_datasheet | Starter record for string sizing tests.
LONGi | Hi-MO 6 | LR5-72HTH-580M | 580 | 43.51 | 13.34 | 51.78 | 14.2 | -0.29 | -0.23 | 0.05 | 2278 | 1134 | 35 | seed_verify_datasheet | Starter record for string sizing tests.
LONGi | Hi-MO 6 | LR5-72HTH-585M | 585 | 43.7 | 13.39 | 51.97 | 14.26 | -0.29 | -0.23 | 0.05 | 2278 | 1134 | 35 | seed_verify_datasheet | Starter record for string sizing tests.
SunPro | SPDG N-type | SPDG430-N108M10 | 430 | [10 empty] | model_only_needs_datasheet | Panel catalog model; datasheet parameters pending.
SunPro | SPDG N-type | SPDG435-N108M10 | 435 | [10 empty] | model_only_needs_datasheet | Panel catalog model; datasheet parameters pending.
SunPro | SPDG N-type | SPDG440-N108M10 | 440 | [10 empty] | model_only_needs_datasheet | Panel catalog model; datasheet parameters pending.
SunPro | SPDG N-type | SPDG570-N144M10 | 570 | [10 empty] | model_only_needs_datasheet | Panel catalog model; datasheet parameters pending.
SunPro | SPDG N-type | SPDG575-N144M10 | 575 | [10 empty] | model_only_needs_datasheet | Panel catalog model; datasheet parameters pending.
SunPro | SPDG N-type | SPDG580-N144M10 | 580 | [10 empty] | model_only_needs_datasheet | Panel catalog model; datasheet parameters pending.
SunPro | SPDG N-type | SPDG585-N144M10 | 585 | [10 empty] | model_only_needs_datasheet | Panel catalog model; datasheet parameters pending.
Trina | Vertex S+ | TSM-NEG9R.25-430 | 430 | [10 empty] | model_only_needs_datasheet | Panel catalog model; datasheet parameters pending.
Trina | Vertex S+ | TSM-NEG9R.25-435 | 435 | [10 empty] | model_only_needs_datasheet | Panel catalog model; datasheet parameters pending.
Trina | Vertex S+ | TSM-NEG9R.25-440 | 440 | [10 empty] | model_only_needs_datasheet | Panel catalog model; datasheet parameters pending.
Trina | Vertex N | TSM-NEG18R.28-500 | 500 | [10 empty] | model_only_needs_datasheet | Panel catalog model; datasheet parameters pending.
Trina | Vertex N | TSM-NEG18R.28-505 | 505 | [10 empty] | model_only_needs_datasheet | Panel catalog model; datasheet parameters pending.
Trina | Vertex N | TSM-NEG18R.28-510 | 510 | [10 empty] | model_only_needs_datasheet | Panel catalog model; datasheet parameters pending.
Trina | Vertex N | TSM-NEG19RC.20-575 | 575 | [10 empty] | model_only_needs_datasheet | Panel catalog model; datasheet parameters pending.
Trina | Vertex N | TSM-NEG19RC.20-580 | 580 | [10 empty] | model_only_needs_datasheet | Panel catalog model; datasheet parameters pending.
Trina | Vertex N | TSM-NEG19RC.20-585 | 585 | [10 empty] | model_only_needs_datasheet | Panel catalog model; datasheet parameters pending.
Trina | Vertex N | TSM-NEG21C.20-700 | 700 | [10 empty] | model_only_needs_datasheet | Panel catalog model; datasheet parameters pending.
Trina | Vertex N | TSM-NEG21C.20-705 | 705 | [10 empty] | model_only_needs_datasheet | Panel catalog model; datasheet parameters pending.
Trina | Vertex N | TSM-NEG21C.20-710 | 710 | [10 empty] | model_only_needs_datasheet | Panel catalog model; datasheet parameters pending.
Ulica | UL N-type | UL-430M-108HV | 430 | [10 empty] | model_only_needs_datasheet | Panel catalog model; datasheet parameters pending.
Ulica | UL N-type | UL-435M-108HV | 435 | [10 empty] | model_only_needs_datasheet | Panel catalog model; datasheet parameters pending.
Ulica | UL N-type | UL-440M-108HV | 440 | [10 empty] | model_only_needs_datasheet | Panel catalog model; datasheet parameters pending.
Ulica | UL N-type | UL-550M-144HV | 550 | [10 empty] | model_only_needs_datasheet | Panel catalog model; datasheet parameters pending.
Ulica | UL N-type | UL-555M-144HV | 555 | [10 empty] | model_only_needs_datasheet | Panel catalog model; datasheet parameters pending.
Ulica | UL N-type | UL-560M-144HV | 560 | [10 empty] | model_only_needs_datasheet | Panel catalog model; datasheet parameters pending.
Ulica | UL N-type | UL-575M-144HV | 575 | [10 empty] | model_only_needs_datasheet | Panel catalog model; datasheet parameters pending.
Ulica | UL N-type | UL-580M-144HV | 580 | [10 empty] | model_only_needs_datasheet | Panel catalog model; datasheet parameters pending.

## Batteries
brand | series | model | chemistry | nominal_energy_kwh | usable_energy_kwh | nominal_voltage_v | capacity_ah | cycle_life_min | cycle_life_max | communication | bms | compatibility | data_status | notes
Pylontech | US Series | US5000 | LiFePO4 | 4.8 |  | 48 |  | 6000 | 8000 | CAN/RS485 | Integrated BMS | Deye compatible | seed_verify_datasheet | User-listed premium battery; verify exact usable energy and protocol settings.
Pylontech | Force L2 | Force L2 | LiFePO4 |  |  |  |  | 6000 | 8000 | CAN/RS485 | Integrated BMS | Deye compatible | model_only_needs_datasheet | User-listed premium low-voltage stack; datasheet parameters pending.
Pylontech | Force H2 | Force H2 | LiFePO4 |  |  |  |  | 6000 | 8000 | CAN/RS485 | Integrated BMS | Deye compatible | model_only_needs_datasheet | User-listed premium high-voltage stack; datasheet parameters pending.
Dyness | BX Series | BX51100 | LiFePO4 | 5.12 |  | 51.2 | 100 |  |  | CAN/RS485 | Integrated BMS | Deye compatible | seed_verify_datasheet | User-listed value battery; verify exact cycle life and protocol settings.
Dyness | PowerRack | PowerRack | LiFePO4 | [6 empty] | CAN/RS485 | Integrated BMS | Deye compatible | model_only_needs_datasheet | User-listed rack battery series; datasheet parameters pending.
Dyness | Tower | Tower | LiFePO4 | [6 empty] | CAN/RS485 | Integrated BMS | Deye compatible | model_only_needs_datasheet | User-listed stack battery series; datasheet parameters pending.
Deye ESS | SE Series | SE-G5.1 | LiFePO4 | 5.12 |  | 51.2 | 100 |  |  | CAN/RS485 | Deye BMS | Deye native | seed_verify_datasheet | Deye ESS model; native protocol expected; verify datasheet.
Deye ESS | SE Series | SE-F5 | LiFePO4 | 5.12 |  | 51.2 | 100 |  |  | CAN/RS485 | Deye BMS | Deye native | model_only_needs_datasheet | Deye ESS model; datasheet parameters pending.
Deye ESS | RW Series | RW-F16 | LiFePO4 | 16 |  | 51.2 |  |  |  | CAN/RS485 | Deye BMS | Deye native | seed_verify_datasheet | Deye ESS high-capacity model; verify exact energy and current limits.
Gobel Power | Rack/Wall | Gobel Power 5.12kWh 51.2V 100Ah | LiFePO4 | 5.12 |  | 51.2 | 100 |  |  | CAN/RS485 | JK/PACE BMS | Deye compatible | model_only_needs_datasheet | User-listed mid-segment supplier; often EVE Grade A+ cells.
Gobel Power | Rack/Wall | Gobel Power 10.24kWh 51.2V 200Ah | LiFePO4 | 10.24 |  | 51.2 | 200 |  |  | CAN/RS485 | JK/PACE BMS | Deye compatible | model_only_needs_datasheet | User-listed mid-segment supplier; datasheet parameters pending.
GSL Energy | Wall/Rack | GSL 5.12kWh 51.2V 100Ah | LiFePO4 | 5.12 |  | 51.2 | 100 |  |  | CAN/RS485 | Integrated BMS | Deye compatible | model_only_needs_datasheet | User-listed supplier; EVE/CATL cells reported by user.
GSL Energy | Wall/Rack | GSL 10.24kWh 51.2V 200Ah | LiFePO4 | 10.24 |  | 51.2 | 200 |  |  | CAN/RS485 | Integrated BMS | Deye compatible | model_only_needs_datasheet | User-listed supplier; datasheet parameters pending.
Felicity ESS | LPBA Series | LPBA48100-OL | LiFePO4 | 5.12 |  | 51.2 | 100 |  |  | CAN/RS485 | Integrated BMS | Deye compatible | model_only_needs_datasheet | Common Felicity low-voltage model candidate; datasheet parameters pending.
Felicity ESS | LPBF Series | LPBF48100-M | LiFePO4 | 5.12 |  | 51.2 | 100 |  |  | CAN/RS485 | Integrated BMS | Deye compatible | model_only_needs_datasheet | Common Felicity low-voltage model candidate; datasheet parameters pending.
HinaESS | Rack/Commercial | HinaESS 5.12kWh 51.2V 100Ah | LiFePO4 | 5.12 |  | 51.2 | 100 |  |  | CAN/RS485 | Integrated BMS | Deye compatible | model_only_needs_datasheet | User-listed commercial battery supplier; datasheet parameters pending.
HinaESS | Rack/Commercial | HinaESS 10.24kWh 51.2V 200Ah | LiFePO4 | 10.24 |  | 51.2 | 200 |  |  | CAN/RS485 | Integrated BMS | Deye compatible | model_only_needs_datasheet | User-listed commercial battery supplier; datasheet parameters pending.
Basen Green | Rack/Wall | Basen Green 5.12kWh 51.2V 100Ah | LiFePO4 | 5.12 |  | 51.2 | 100 |  |  | CAN/RS485 | Integrated BMS | Deye compatible | model_only_needs_datasheet | OEM battery candidate; datasheet parameters pending.
Basen Green | Rack/Wall | Basen Green 10.24kWh 51.2V 200Ah | LiFePO4 | 10.24 |  | 51.2 | 200 |  |  | CAN/RS485 | Integrated BMS | Deye compatible | model_only_needs_datasheet | OEM battery candidate; datasheet parameters pending.
HTE | Rack/Wall | HTE 5.12kWh 51.2V 100Ah | LiFePO4 | 5.12 |  | 51.2 | 100 |  |  | CAN/RS485 | Integrated BMS | Deye compatible | model_only_needs_datasheet | OEM battery candidate; datasheet parameters pending.
SRNE ESS | Rack/Wall | SRNE ESS 5.12kWh 51.2V 100Ah | LiFePO4 | 5.12 |  | 51.2 | 100 |  |  | CAN/RS485 | Integrated BMS | Deye compatible | model_only_needs_datasheet | OEM battery candidate; datasheet parameters pending.
Hinen | Rack/Wall | Hinen 5.12kWh 51.2V 100Ah | LiFePO4 | 5.12 |  | 51.2 | 100 |  |  | CAN/RS485 | Integrated BMS | Deye compatible | model_only_needs_datasheet | OEM battery candidate; datasheet parameters pending.
Svolt ESS | Rack/Wall | Svolt ESS 5.12kWh 51.2V 100Ah | LiFePO4 | 5.12 |  | 51.2 | 100 |  |  | CAN/RS485 | Integrated BMS | Deye compatible | model_only_needs_datasheet | OEM battery candidate; datasheet parameters pending.
EVE Energy ESS | Rack/Wall | EVE Energy ESS 5.12kWh 51.2V 100Ah | LiFePO4 | 5.12 |  | 51.2 | 100 |  |  | CAN/RS485 | Integrated BMS | Deye compatible | model_only_needs_datasheet | OEM battery candidate; datasheet parameters pending.

## Mounting
Количество крепежа (Mounting quantity) | Значение (Value) | Ед. изм. (Unit) | Формула / смысл (Formula / meaning)
Тип кровли (Roof type) |  |  | Из листа Inputs (From Inputs)
Всего панелей (Total panels) |  | pcs | Из листа Inputs (From Inputs)
Панелей в ряду (Panels per row) |  | pcs | Из листа Inputs (From Inputs)
Ряды (Rows) |  | rows | Calculated from total panels and panels per row
Линии реек (Rail lines) |  | pcs | Две линии реек на ряд (Two rail lines per row)
Оценочная длина реек (Estimated rail length) |  | m | Всего панелей x длина рейки на панель x 2 (Total panels x rail length per panel x 2)
Стыки реек (Rail joints) |  | pcs | Оценка по длине реек и складской длине (Estimated from rail length and stock length)
Запас (Reserve) |  | % | Дополнительный запас количества (Extra quantity reserve)
Компонент (Component) | Количество (Quantity) | Ед. изм. (Unit) | Примечания (Notes)
Крюки / фальцевые зажимы / наземные стойки (Roof hooks / seam clamps / ground posts) |  | pcs | Крюки, фальцевые зажимы или наземные стойки по типу установки (Hooks, seam clamps, or ground posts depending on installation type)
Мини-рельсы (Mini-rails) |  | pcs | Для кровельных систем с мини-рельсами (Used for mini-rail roof systems)
Рейки (Rails) |  | pcs | Складские отрезки реек (Rail stock pieces)
Соединители реек (Rail connectors) |  | pcs | Обычно два на стык рейки (Usually two per rail joint)
Крайние прижимы (End clamps) |  | pcs | Четыре на ряд (Four per row)
Средние прижимы (Middle clamps) |  | pcs | Два на промежуток между панелями в ряду (Two per gap between panels in a row)
Комплекты болтов (Bolt sets) |  | pcs | Запас крепежа (Fastener allowance)
Клипсы заземления (Grounding clips) |  | pcs | Стартово один на панель (One per panel starter assumption)
Кабельные клипсы (Cable clips) |  | pcs | Стартово два на панель (Two per panel starter assumption)

## Equipment
Category | Показатель (Item) | Количество (Quantity) | Ед. изм. (Unit) | Примечания (Notes)
Инвертор (Inverter) |  | 1 | pcs | Выбранный инвертор (Selected inverter)
Solar panels |  |  | pcs | Total panel quantity
АКБ (Battery) |  |  | pcs | Selected battery quantity
Battery energy |  |  | kWh | Total nominal battery energy
Mounting | Крюки / фальцевые зажимы / наземные стойки (Roof hooks / seam clamps / ground posts) |  | pcs | From Mounting sheet
Mounting | Мини-рельсы (Mini-rails) |  | pcs | From Mounting sheet
Mounting | Рейки (Rails) |  | pcs | From Mounting sheet
Mounting | Соединители реек (Rail connectors) |  | pcs | From Mounting sheet
Mounting | Крайние прижимы (End clamps) |  | pcs | From Mounting sheet
Mounting | Средние прижимы (Middle clamps) |  | pcs | From Mounting sheet
Mounting | Комплекты болтов (Bolt sets) |  | pcs | From Mounting sheet
Mounting | Клипсы заземления (Grounding clips) |  | pcs | From Mounting sheet
Mounting | Кабельные клипсы (Cable clips) |  | pcs | From Mounting sheet
Protection | PV cable red |  | m | From CableProtection sheet
Protection | PV cable black |  | m | From CableProtection sheet
Protection | PE cable |  | m | From CableProtection sheet
Protection | DC string fuses |  | pcs | From CableProtection sheet
Protection | DC isolator |  | pcs | From CableProtection sheet
Protection | DC SPD Type 2 |  | pcs | From CableProtection sheet
Protection | AC breaker |  | pcs | From CableProtection sheet
Protection | AC SPD Type 2 |  | pcs | From CableProtection sheet
Protection | AC cable |  | m | From CableProtection sheet
Protection | Battery DC cable pair |  | pair | From CableProtection sheet
Protection | Battery fuse or breaker |  | pcs | From CableProtection sheet
Sizing | Recommended DC cable section |  | mm2 | Starter sizing; verify installation method
Sizing | DC voltage drop |  | % | Starter voltage-drop estimate
Sizing | Recommended AC cable section |  | mm2 | Starter sizing; verify installation method
Sizing | AC voltage drop |  | % | Starter voltage-drop estimate
Sizing | Recommended battery cable section |  | mm2 | Starter sizing; verify installation method
Sizing | Estimated battery current |  | A | Inverter power / battery voltage
Sizing | Коэффициент снижения нагрузки кабеля (Cable derating factor) |  | factor | Grouping x ambient derating
Protection | Recommended SPD type |  |  | Starter selection; verify local standards
Protection | Система заземления AC (AC earthing system) |  |  | Selected earthing checklist
Documentation | Datasheet verification | 1 | task | Required before commercial use

## CableProtection
Cable / Protection item | Количество (Quantity) | Ед. изм. (Unit) | Формула / смысл (Formula / meaning)
PV cable red |  | m | Длина DC кабеля (DC cable route length)
PV cable black |  | m | Длина DC кабеля (DC cable route length)
PE cable |  | m | Grounding route length
DC string fuses |  | pcs | Used when strings per MPPT > 1
DC isolator |  | pcs | Starter quantity
DC SPD Type 2 |  | pcs | Starter quantity
AC breaker |  | pcs | Starter quantity; rating must be selected
AC SPD Type 2 |  | pcs | Starter quantity
AC cable |  | m | Длина AC кабеля (AC cable route length)
Battery DC cable pair |  | pair | Starter quantity
Battery fuse or breaker |  | pcs | Starter quantity; rating must be selected
Protection design status |  |  | VERIFY until ratings and cable sections are selected
Sizing result |  | Ед. изм. (Unit) | Формула / смысл (Formula / meaning)
Recommended DC cable section |  | mm2 | Based on PV operating current
DC voltage drop |  | % | 2 x length x current x copper resistance / section / voltage
Suggested DC fuse rating |  | A | Based on string short-circuit current
Estimated AC current |  | A | Based on inverter AC power and phase
Recommended AC cable section |  | mm2 | Based on estimated AC current
AC voltage drop |  | % | Starter single/three-phase voltage-drop estimate
Suggested AC breaker rating |  | A | Next common rating above AC current
Estimated battery current |  | A | AC power / battery nominal voltage
Recommended battery cable section |  | mm2 | Based on estimated battery current
Suggested battery breaker rating |  | A | Next common rating above battery current
Sizing status |  |  | VERIFY until local standards and datasheets are checked
Advanced protection result |  | Ед. изм. (Unit) | Формула / смысл (Formula / meaning)
Recommended SPD type |  |  | Based on selected lightning protection condition
Система заземления AC (AC earthing system) |  |  | Selected earthing system checklist
Combined cable derating factor |  | factor | Grouping derating x ambient derating
Derated DC cable ampacity |  | A | Selected DC cable ampacity after derating
Advanced protection status |  |  | VERIFY until local standards are checked

## BulkCompatibility
Scenario | Инвертор (Inverter) | Панель (Panel) | АКБ (Battery) | Panels/string | Strings/MPPT | Cold string Voc | Hot string Vmp | PV voltage | PV current | АКБ (Battery) | Overall | Примечания (Notes)
Residential 5kW Deye | SUN-5K-SG03LP1-EU | JKM575N-72HL4-V | US5000 | 8 | 1 | [6 empty] | Starter Deye LV scenario.
Residential 8kW Deye | SUN-8K-SG01LP1-EU | JKM575N-72HL4-V | US5000 | 8 | 2 | [6 empty] | Starter two-string Deye LV scenario.
Residential 6kW Deye | SUN-6K-SG03LP1-EU | LR5-72HTH-580M | BX51100 | 8 | 1 | [6 empty] | Starter LONGi plus Dyness scenario.
Commercial 10kW Deye | SUN-10K-SG02LP1-EU-AM3-P | TSM-NEG18R.28-500 | SE-G5.1 | 8 | 1 | [6 empty] | Model-only scenario; datasheet values pending.
Hybrid 12kW Deye | SUN-12K-SG02LP1-EU-AM3-P | JAM54D40-440/LB | SE-G5.1 | 8 | 1 | [6 empty] | Model-only scenario; datasheet values pending.
Growatt hybrid | SPH 10000TL3 BH-UP | JKM575N-72HL4-V | US5000 | 8 | 1 | [6 empty] | Needs datasheet verification for exact Growatt electrical limits.
Solis hybrid | S6-EH3P10K-H-EU | JKM575N-72HL4-V | BX51100 | 8 | 1 | [6 empty] | Needs datasheet verification for exact Solis electrical limits.
MUST hybrid | PV1800 PRO-5.2KW-48V | JKM575N-72HL4-V | US5000 | 4 | 1 | [6 empty] | Low-voltage starter check.

## Economics
Экономика (Economics) | Значение (Value) | Ед. изм. (Unit) | Формула / смысл (Formula / meaning)
Регион / тарифная зона (Region / tariff zone) |  |  | Из листа Inputs (From Inputs)
Мощность выбранной панели (Selected panel power) |  | W | Из базы Panels (From Panels database)
Total panel count |  | pcs | Из листа Inputs (From Inputs)
Мощность СЭС (PV system size) |  | kWp | Panel power x total panels
Удельная выработка (Specific yield) |  | kWh/kWp/year | Из базы Regions (From Regions database)
Коэффициент производительности (Performance ratio) | 0.85 | factor | Стартовый коэффициент потерь системы (Starter system loss factor)
Годовая выработка (Annual generation) |  | kWh/year | Мощность PV x выработка x коэффициент производительности (PV size x yield x performance ratio)
Розничный тариф (Retail tariff) |  | RUB/kWh | Из базы Tariffs (From Tariffs database)
Экспорт / зеленый тариф (Export / green tariff) |  | RUB/kWh | Стартовая цена покупки микрогенерации (Starter microgeneration purchase value)
Доля собственного потребления (Self-consumption share) |  | % | Из листа Inputs (From Inputs)
Годовая экономия (Annual savings) |  | RUB/year | Self-consumed value plus exported value
Простая окупаемость (Simple payback) |  | years | Стоимость системы / годовая экономия (Installed cost / annual savings)
Стоимость установленной системы (Installed system cost) |  | RUB | Из листа Inputs (From Inputs)
Статус источника тарифа (Tariff source status) |  |  | VERIFY until supplier/date is checked
Источник розничного тарифа (Retail tariff source) |  |  | URL источника (Source URL)
Источник экспортного тарифа (Export tariff source) |  |  | URL источника (Source URL)
Потребление в месяц (Monthly consumption) |  | kWh/month | Из листа Inputs (From Inputs)
Годовое потребление (Annual consumption) |  | kWh/year | Месячное потребление x 12 (Monthly consumption x 12)
Целевое годовое покрытие (Target annual coverage) |  | kWh/year | Годовое потребление x целевое покрытие (Annual consumption x target coverage)
Смешанный тариф день-ночь (Day-night blended tariff) |  | RUB/kWh | Доля дня x дневной тариф плюс доля ночи x ночной тариф (Day share x day tariff plus night share x night tariff)
Оценочная текущая годовая стоимость (Estimated current annual cost) |  | RUB/year | Годовое потребление x розничный тариф (Annual consumption x retail tariff)
Оценочная годовая стоимость день-ночь (Estimated day-night annual cost) |  | RUB/year | Годовое потребление x смешанный тариф день-ночь (Annual consumption x blended day-night tariff)
Потенциальная экономия день-ночь до СЭС (Potential day-night saving before PV) |  | RUB/year | Текущая стоимость минус стоимость день-ночь (Current cost minus day-night cost)

## SystemOptions
Вариант (Option) | Качество (Quality) | Стоимость за кВтп (Cost per kWp) | Срок службы (Service life) | Деградация (Degradation) | Требуемая годовая выработка (Required annual generation) | Требуемая мощность кВтп (Required kWp) | Рекомендуемая мощность кВтп (Recommended kWp) | Панели (Panels) | Дневная выработка (Daily generation) | Месячная выработка (Monthly generation) | Годовая выработка (Annual generation) | Покрытие (Coverage) | Оценочная стоимость (Estimated cost) | Экономия на едином тарифе (Single-rate savings) | Экономия день-ночь (Day-night savings) | Выручка от зеленого тарифа (Green tariff export revenue) | Окупаемость день-ночь (Payback day-night) | Примечания (Notes)
Premium | [17 empty] | Повышенный бюджет; сверить коммерческое предложение (Higher allowance; verify commercial offer)
Standard | [17 empty] | Сбалансированный вариант по умолчанию (Balanced default option)
Economy | [17 empty] | Пониженный бюджет; проверить гарантии (Lower cost allowance; verify warranties)

## Lifetime
Год (Year) | Выработка Premium (Premium generation) | Выработка Standard (Standard generation) | Выработка Economy (Economy generation) | Накопительно Premium (Premium cumulative) | Накопительно Standard (Standard cumulative) | Накопительно Economy (Economy cumulative)
0
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20

## OptionTiers
tier | quality_level | cost_rub_per_kwp | panel_service_life_years | panel_degradation_pct_year | notes
Premium | premium | 105000 | 25 | 0.4 | Higher equipment and installation allowance; verify commercial offer.
Standard | base | 85000 | 25 | 0.5 | Balanced default option for most customers; verify commercial offer.
Economy | economy | 70000 | 20 | 0.7 | Lower cost allowance; verify component quality and warranty.

## MonthlyGeneration
Месяц (Month) | Выработка (Generation) | Потребление (Consumption) | Собственное потребление (Self-consumed) | Стоимость собственного потребления (Self-consumption value) | Экспортировано (Exported) | Стоимость экспорта (Export value) | Общая стоимость (Total value) | Покрытие (Coverage)
Янв (Jan)
Фев (Feb)
Мар (Mar)
Апр (Apr)
Май (May)
Июн (Jun)
Июл (Jul)
Авг (Aug)
Сен (Sep)
Окт (Oct)
Ноя (Nov)
Дек (Dec)
Итого (Total)

## MonthlyYieldProfile
region | jan_pct | feb_pct | mar_pct | apr_pct | may_pct | jun_pct | jul_pct | aug_pct | sep_pct | oct_pct | nov_pct | dec_pct | data_status | notes
Moscow starter | 3 | 5 | 8 | 11 | 13 | 14 | 14 | 12 | 9 | 6 | 3 | 2 | seed_verify_source | Starter seasonal split; verify exact site with PVGIS or Global Solar Atlas.
Saint Petersburg starter | 2 | 4 | 8 | 11 | 14 | 15 | 15 | 12 | 9 | 5 | 3 | 2 | seed_verify_source | Starter seasonal split; verify exact site with PVGIS or Global Solar Atlas.
Krasnodar starter | 5 | 6 | 9 | 10 | 12 | 13 | 13 | 12 | 9 | 6 | 4 | 3 | seed_verify_source | Starter seasonal split; verify exact site with PVGIS or Global Solar Atlas.
Rostov-on-Don starter | 4 | 6 | 9 | 11 | 12 | 13 | 13 | 12 | 9 | 6 | 3 | 2 | seed_verify_source | Starter seasonal split; verify exact site with PVGIS or Global Solar Atlas.
Yekaterinburg starter | 3 | 5 | 9 | 11 | 13 | 14 | 14 | 11 | 9 | 6 | 3 | 2 | seed_verify_source | Starter seasonal split; verify exact site with PVGIS or Global Solar Atlas.

## CableSizing
section_mm2 | ampacity_a | notes
1.5 | 0 | Lookup floor for low-current auxiliary AC circuits; verify installation method.
2.5 | 25 | Starter copper cable ampacity assumption; verify installation method.
4 | 35 | Starter copper cable ampacity assumption; verify installation method.
6 | 50 | Starter copper cable ampacity assumption; verify installation method.
10 | 70 | Starter copper cable ampacity assumption; verify installation method.
16 | 90 | Starter copper cable ampacity assumption; verify installation method.
25 | 120 | Starter copper cable ampacity assumption; verify installation method.
35 | 150 | Starter copper cable ampacity assumption; verify installation method.
50 | 180 | Starter copper cable ampacity assumption; verify installation method.
70 | 230 | Starter copper cable ampacity assumption; verify installation method.
95 | 280 | Starter copper cable ampacity assumption; verify installation method.
120 | 330 | Starter copper cable ampacity assumption; verify installation method.

## ProtectionRules
section_mm2 | ampacity_a | notes
1.5 | 0 | Lookup floor for low-current auxiliary AC circuits; verify installation method.
2.5 | 25 | Starter copper cable ampacity assumption; verify installation method.
4 | 35 | Starter copper cable ampacity assumption; verify installation method.
6 | 50 | Starter copper cable ampacity assumption; verify installation method.
10 | 70 | Starter copper cable ampacity assumption; verify installation method.
16 | 90 | Starter copper cable ampacity assumption; verify installation method.
25 | 120 | Starter copper cable ampacity assumption; verify installation method.
35 | 150 | Starter copper cable ampacity assumption; verify installation method.
50 | 180 | Starter copper cable ampacity assumption; verify installation method.
70 | 230 | Starter copper cable ampacity assumption; verify installation method.
95 | 280 | Starter copper cable ampacity assumption; verify installation method.
120 | 330 | Starter copper cable ampacity assumption; verify installation method.
PV cable red | DC cable | 0 | m | user_input | Positive DC cable length; user-defined route length.
PV cable black | DC cable | 0 | m | user_input | Negative DC cable length; user-defined route length.
PE cable | Grounding cable | 0 | m | user_input | Protective earth cable length; user-defined route length.
DC string fuse | DC protection | 0 | pcs | strings_per_mppt_gt_1 | Use when parallel strings are connected; verify by module Isc and local rules.
DC isolator | DC protection | 1 | pcs | one_per_inverter | DC isolator or switch-disconnector; verify inverter built-in equipment.
DC SPD Type 2 | DC protection | 1 | pcs | one_per_array | DC surge protection starter assumption.
AC breaker | AC protection | 1 | pcs | one_per_inverter | AC breaker rating must be selected by inverter output current and local rules.
AC SPD Type 2 | AC protection | 1 | pcs | one_per_system | AC surge protection starter assumption.
AC cable | AC cable | 0 | m | user_input | AC cable length; user-defined route length.
Battery DC cable pair | Battery cable | 1 | pair | one_per_battery_stack | Battery cable pair starter assumption.
Battery fuse or breaker | Battery protection | 1 | pcs | one_per_battery_stack | Battery protection must be selected by battery/inverter current.

## SpdRules
condition | recommended_spd | notes
No external LPS | Type 2 DC/AC SPD | Starter residential/commercial assumption; verify risk assessment and local standards.
External LPS | Type 1+2 DC/AC SPD | Use when building has external lightning protection system; verify coordination.
Overhead supply | Type 1+2 AC SPD | Often required on AC side with overhead supply; verify utility and standards.
Long outdoor DC route | Type 2 DC SPD near inverter and array | May require additional SPD placement; verify cable route and inverter manual.

## EarthingRules
earthing_system | starter_requirement | notes
TN-S | PE continuity and bonding check | Verify PE conductor sizing | equipotential bonding | and SPD connection length.
TN-C-S | Separate PEN/PE handling check | Verify local rules for PV connection | bonding | and SPD earthing.
TT | RCD and earth electrode check | Verify electrode resistance | RCD coordination | and SPD discharge path.
IT | Special protection study required | Do not use starter assumptions without engineering verification.

## CableDerating
factor_type | option | default_factor | notes
installation_method | Open air | 1 | Starter assumption for ventilated cable routes; verify local tables.
installation_method | Conduit or trunking | 0.85 | Starter derating for enclosed routes; verify local tables.
installation_method | Thermal insulation | 0.65 | High derating risk; verify local tables.
grouping | Single circuit | 1 | No grouping derating applied.
grouping | Several circuits | 0.8 | Starter grouping derating; verify actual routing.
temperature | Standard ambient | 1 | Starter assumption.
temperature | High ambient | 0.87 | Starter derating for hot environments; verify cable rating.

## MountingRules
roof_type | component | base_qty | qty_per_panel | qty_per_row | qty_per_joint | qty_per_string | qty_per_array | rounding_unit | notes
Metal tile | Roof hook | 0 | 4 | 0 | 0 | 0 | 0 | 1 | Use 4 hooks per panel as starter assumption; verify by rail span and wind zone.
Metal tile | Rail | 0 | 2 | 0 | 0 | 0 | 0 | 1 | Two rails per panel row equivalent; final length depends on module width and rail stock length.
Metal tile | Rail connector | 0 | 0 | 0 | 2 | 0 | 0 | 1 | Two connectors per rail joint.
Metal tile | End clamp | 0 | 0 | 4 | 0 | 0 | 0 | 1 | Four end clamps per row.
Metal tile | Middle clamp | 0 | 2 | 0 | 0 | 0 | 0 | 1 | Two middle clamps per gap between adjacent panels; formula handles gaps.
Metal tile | Bolt set | 0 | 4 | 0 | 0 | 0 | 0 | 1 | Starter one bolt set per hook.
Metal tile | Grounding clip | 0 | 1 | 0 | 0 | 0 | 0 | 1 | One grounding clip per module.
Metal tile | Cable clip | 0 | 2 | 0 | 0 | 0 | 0 | 1 | Two cable clips per module.
Standing seam | Mini rail clamp | 0 | 4 | 0 | 0 | 0 | 0 | 1 | Use seam clamps or mini-rail clamps; verify seam spacing and clamp approval.
Standing seam | Mini rail | 0 | 2 | 0 | 0 | 0 | 0 | 1 | Two mini-rail supports per module as starter assumption.
Standing seam | Rail connector | 0 | 0 | 0 | 2 | 0 | 0 | 1 | Only used when continuous rail is selected.
Standing seam | End clamp | 0 | 0 | 4 | 0 | 0 | 0 | 1 | Four end clamps per row.
Standing seam | Middle clamp | 0 | 2 | 0 | 0 | 0 | 0 | 1 | Two middle clamps per panel gap.
Standing seam | Bolt set | 0 | 4 | 0 | 0 | 0 | 0 | 1 | Starter one bolt set per clamp.
Standing seam | Grounding clip | 0 | 1 | 0 | 0 | 0 | 0 | 1 | One grounding clip per module.
Standing seam | Cable clip | 0 | 2 | 0 | 0 | 0 | 0 | 1 | Two cable clips per module.
Trapezoidal sheet | Mini rail | 0 | 2 | 0 | 0 | 0 | 0 | 1 | Two mini-rails per module as starter assumption.
Trapezoidal sheet | Self-drilling screw set | 0 | 8 | 0 | 0 | 0 | 0 | 1 | Four screws per mini-rail pair side as starter assumption.
Trapezoidal sheet | Rail connector | 0 | 0 | 0 | 2 | 0 | 0 | 1 | Only used when long rails are selected.
Trapezoidal sheet | End clamp | 0 | 0 | 4 | 0 | 0 | 0 | 1 | Four end clamps per row.
Trapezoidal sheet | Middle clamp | 0 | 2 | 0 | 0 | 0 | 0 | 1 | Two middle clamps per panel gap.
Trapezoidal sheet | Bolt set | 0 | 4 | 0 | 0 | 0 | 0 | 1 | Starter fastener set allowance.
Trapezoidal sheet | Grounding clip | 0 | 1 | 0 | 0 | 0 | 0 | 1 | One grounding clip per module.
Trapezoidal sheet | Cable clip | 0 | 2 | 0 | 0 | 0 | 0 | 1 | Two cable clips per module.
Flat roof | Triangle support | 0 | 1 | 0 | 0 | 0 | 0 | 1 | One support set per panel as starter assumption.
Flat roof | Rail | 0 | 2 | 0 | 0 | 0 | 0 | 1 | Two rails per panel row equivalent.
Flat roof | Rail connector | 0 | 0 | 0 | 2 | 0 | 0 | 1 | Two connectors per rail joint.
Flat roof | End clamp | 0 | 0 | 4 | 0 | 0 | 0 | 1 | Four end clamps per row.
Flat roof | Middle clamp | 0 | 2 | 0 | 0 | 0 | 0 | 1 | Two middle clamps per panel gap.
Flat roof | Bolt set | 0 | 4 | 0 | 0 | 0 | 0 | 1 | Starter fastener set allowance.
Flat roof | Grounding clip | 0 | 1 | 0 | 0 | 0 | 0 | 1 | One grounding clip per module.
Flat roof | Cable clip | 0 | 2 | 0 | 0 | 0 | 0 | 1 | Two cable clips per module.
Ground mount | Ground post | 0 | 0 | 2 | 0 | 0 | 0 | 1 | Two ground posts per row as starter assumption; verify soil and wind load.
Ground mount | Ground rail | 0 | 2 | 0 | 0 | 0 | 0 | 1 | Two rails per panel row equivalent for ground structure.
Ground mount | Rail connector | 0 | 0 | 0 | 2 | 0 | 0 | 1 | Two connectors per rail joint.
Ground mount | End clamp | 0 | 0 | 4 | 0 | 0 | 0 | 1 | Four end clamps per row.
Ground mount | Middle clamp | 0 | 2 | 0 | 0 | 0 | 0 | 1 | Two middle clamps per panel gap.
Ground mount | Bolt set | 0 | 6 | 0 | 0 | 0 | 0 | 1 | Starter fastener set allowance for ground structure.
Ground mount | Grounding clip | 0 | 1 | 0 | 0 | 0 | 0 | 1 | One grounding clip per module.
Ground mount | Cable clip | 0 | 2 | 0 | 0 | 0 | 0 | 1 | Two cable clips per module.

## Regions
region | specific_yield_kwh_per_kwp_year | source_url | data_status | notes
Moscow starter | 950 | https://globalsolaratlas.info/ | seed_verify_source | Starter annual yield assumption; verify exact site with PVGIS or Global Solar Atlas.
Saint Petersburg starter | 850 | https://globalsolaratlas.info/ | seed_verify_source | Starter annual yield assumption; verify exact site with PVGIS or Global Solar Atlas.
Krasnodar starter | 1300 | https://globalsolaratlas.info/ | seed_verify_source | Starter annual yield assumption; verify exact site with PVGIS or Global Solar Atlas.
Rostov-on-Don starter | 1250 | https://globalsolaratlas.info/ | seed_verify_source | Starter annual yield assumption; verify exact site with PVGIS or Global Solar Atlas.
Yekaterinburg starter | 1050 | https://globalsolaratlas.info/ | seed_verify_source | Starter annual yield assumption; verify exact site with PVGIS or Global Solar Atlas.

## Tariffs
region | retail_tariff_rub_kwh | export_tariff_rub_kwh | retail_source_url | export_source_url | data_status | notes
Moscow starter | 8.5 | 3.5 | https://www.mosenergosbyt.ru/ | https://www.atsenergo.ru/ | seed_verify_source | Retail tariff: verify with regional supplier/regulator. Export price: verify through ATS market-price data used for microgeneration surplus purchase.
Saint Petersburg starter | 7.8 | 3.3 | https://www.pes.spb.ru/ | https://www.atsenergo.ru/ | seed_verify_source | Retail tariff: verify with regional supplier/regulator. Export price: verify through ATS market-price data used for microgeneration surplus purchase.
Krasnodar starter | 7.2 | 3.2 | https://kuban.tns-e.ru/ | https://www.atsenergo.ru/ | seed_verify_source | Retail tariff: verify with regional supplier/regulator. Export price: verify through ATS market-price data used for microgeneration surplus purchase.
Rostov-on-Don starter | 7.3 | 3.2 | https://rostov.tns-e.ru/ | https://www.atsenergo.ru/ | seed_verify_source | Retail tariff: verify with regional supplier/regulator. Export price: verify through ATS market-price data used for microgeneration surplus purchase.
Yekaterinburg starter | 7 | 3.1 | https://ekb.esplus.ru/ | https://www.atsenergo.ru/ | seed_verify_source | Retail tariff: verify with regional supplier/regulator. Export price: verify through ATS market-price data used for microgeneration surplus purchase.

## Compatibility
Матрица совместимости (Compatibility Matrix) | Статус (Status) | Причина (Reason) | Источник (Source)
Выбранный инвертор (Selected inverter) |  |  | Inputs
Выбранная панель (Selected panel) |  |  | Inputs
Выбранная АКБ (Selected battery) |  |  | Inputs
Напряжение/ток PV (PV voltage/current) |  |  | Results
Совместимость АКБ (Battery compatibility) |  |  | Batteries
Полнота данных (Data completeness) |  |  | Databases
Общая совместимость (Overall compatibility) |  |  | Сводный результат (Combined result)
Проверка (Check) | Статус (Status) | Причина (Reason) | Следующее действие (Next action)
Холодный Voc против max PV voltage (Cold Voc vs max PV voltage) |  |  | Изменить панели в строке или инвертор (Adjust panels per string or inverter)
Горячий Vmp против диапазона MPPT (Hot Vmp vs MPPT range) |  |  | Изменить панели в строке (Adjust panels per string)
Ток панели против тока MPPT (Panel current vs MPPT current) |  |  | Изменить строки на MPPT или инвертор (Adjust strings per MPPT or inverter)
Протокол АКБ (Battery protocol) |  |  | Проверить настройки CAN/RS485 (Verify CAN/RS485 settings)
Требуемые данные datasheet (Required datasheet data) |  |  | Заполнить недостающие поля базы (Fill missing database fields)